## Title (hidden)
HITACHI |  |  |  |  | CT / VT |  |  | Contract No. |  | N-19957.1-DF5W
[5 empty] | ADEQUACY CHECK |  |  | Date |  | 2026-03-25
[5 empty] | LT14 - LEWIS 400/132kV SUBSTATION |  |  | Document No. |  | -
[8 empty] | Revision No. |  | A
Prep. By | AP | Checked By |  | RB | Title Sheet |  |  | Contractor |  | HITACHI
LT14 - LEWIS 400/132kV SUBSTATION
CT/VT ADEQUACY CHECK
CT & VT CALCULATIONS
Hitachi
Substation Automation Systems
[7 empty] | Date: |  | 2026-03-25
[7 empty] | Prepared by: |  | Arulprakasam K
[7 empty] | Checked by: |  | Ramesh Babu
[7 empty] | Approved by: |  | Rudresh N

## INDEX (hidden)
HITACHI |  |  |  | CT / VT |  | Contract No. |  | N-19957.1-DF5W
|  |  |  | ADEQUACY CHECK |  | Date |  | 2026-03-25
|  |  |  | LT14 - LEWIS 400/132kV SUBSTATION |  | Document No. |  | -
[6 empty] | Revision No. |  | A
Prep. By | AP | Checked By | RB | Index |  | Contractor |  | HITACHI
INDEX
Pg:No
| 1 | NOTES |  |  | Page 4 of 25 |  |  | 3
| 2 | SUMMARY SHEET |  |  | Page 5 of 25 |  |  | 4 | CT / VT Data Summary
| 3 | CT/VT BURDEN DETAILS |  |  |  |  | - | 11
| 4 | CT ADEQUACY CHECK | [5 empty] | 13
| 5 | PARAMETERS AND FAULT CALCULATIONS |  |  |  |  | - | 14 | Parameters & Fault Calculations
| 6 | BUS SECTION COUPLER | [5 empty] | 18
| 7 | TRANSFORMER FEEDER | [5 empty] | 30
| 8 | LINE PROTECTION 400KV FEEDERS | [5 empty] | 40
| 9 | LINE PROTECTION HVDC FEEDERS | [5 empty] | 59
| 10 | VT ADEQUACY CHECK | [5 empty] | 78
| 11 | HVDC FEEDER VT | [5 empty] | 79
| 12 | FEEDER VT | [5 empty] | 84
| 13 | SGT 1,2 &3 VT | [5 empty] | 89
Supporting Documents
| ANNEXURE-A |  | Over All SLD |  |  |  |  | 92 |  | Annexure- A | Relays Burden
| ANNEXURE-B |  | Input requirements list |  |  |  |  | 94 |  | Annexure- B | CT requirements of RET670
| ANNEXURE-C |  | CT requirements of RED670 |  |  |  |  | 99 |  | Annexure- C | CT requirements of RET615
| ANNEXURE-D |  | CT requirements of REF650 |  |  |  |  | 109 |  | Annexure- D | CT requirements of REF615
| ANNEXURE-E |  | CT requirements of REC670 |  |  |  |  | 119 |  | Annexure- E | ESI Standard 48-3
| ANNEXURE-F |  | CT requirements of REB500 |  |  |  |  | 123
| ANNEXURE-G |  | CT requirements of P545 |  |  |  |  | 127 |  | Annexure- E | ESI Standard 48-3
| ANNEXURE-H |  | CT requirements of 7SL86 |  |  |  |  | 249 |  | Annexure- F | 220kV SS-516 SLD
| ANNEXURE-I |  | CT requirements of SEL487E |  |  |  |  | 255
| ANNEXURE-H |  | CT requirements of IDM+X |  |  |  |  | 137
| ANNEXURE-I |  | CT requirements of P743 |  |  |  |  | 142
| ANNEXURE-J |  | CT requirements of MFAC |  |  |  |  | 147

## Notes Or Assumptions (hidden)
HITACHI |  |  |  |  | CT / VT | Contract No. | N-19957.1-DF5W
[5 empty] | ADEQUACY CHECK | Date | 2026-03-25
[5 empty] | LT14 - LEWIS 400/132kV SUBSTATION | Document No. | -
[6 empty] | Revision No. | A
Prep. By |  | AP | Checked By | RB | Notes | Contractor | HITACHI
Notes
| 1 | The maximum CT lead length from the SWGR CT secondary terminal to relay terminals are considered as 150m
| 2 | Size of the CT lead considered as 2.5 Sq. mm for calculation | [5 empty] | 165m Lead Resistance of the current loop from the 33kV Incomer SWGR to 220kV Transformer Protection Panel.
| 3 | The maximum VT lead length from the VT secondary terminal to relay terminals are considered as 150m
| 4 | Size of the VT lead considered as 2.5 Sq. mm for calculation
| 5 | Bus fault level is considered as 63kA for 400kV
| 6 | X/R ratio is considered as 50 for 400kV system.
Notes
1. CT Adequacy Check calculation of Remote End Cable Feeders are part of different submission
2. The CT sizing calculation is done for two type of relays RED670 and 7SD522 for cable feeders
3. Class X type CTs are proposed against that of Class TPS type CTs as per SOW
Note:
|  |  |  | 1 | This Calculation is Applicable for all the three S/S
2
MV Max. Bus fault level/Switchgear Rating is assumed as 31.5kA as per Specification S-AAA-GEN-SFL (REV.0-2011) clause 3
MV X/R Ratio is assumed as 15
LV Max. Bus fault level/Switchgear Rating is assumed as 25kA as per Specification S-AAA-GEN-SFL (REV.0-2011) clause 3
LV X/R Ratio is assumed as 15
Power Cable Type is assumed as CU XLPE type .
Positive Sequence Resistance, Positive Sequence Reactance , Zero Sequence Resistance and Zero Sequence Reactance of the power cable are assumed
Route Length of the power cable is assumed as 5km
Minimum 33kV Busbar Fault Current is Assumed as 20kA
33/11kV Transformer Impedance is Assumed to be 12%
Back to
INDEX

## CT-VT Data landscape (hidden)
HITACHI | [6 empty] | CT / VT ADEQUACY CHECK | [9 empty] | Contract No. | N-19957.1-DF5W
[17 empty] | Date | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [9 empty] | Document No. | -
[17 empty] | Revision No. | A
Prep. By |  | AP | Checked By |  |  | RB | Summary Sheet | [9 empty] | Contractor | HITACHI
CT parameters (Summary)
220/132kV Over All Transformer Differential (320MVA) Q08, Q13
(Transformer Differential - 132kV side CT)
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
BC1 | Core1 |  | 1500 |  | 1 | 50 | 2.5 | PX |  | 3 |  | 1500 |  | 37.76 | RET670 | Suitably Dimensioned |  | 94.1432
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
(Transformer Differential - 220kV side CT)
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T12 | Core1 |  | 1200 |  | 1 | 50 | 2.5 | PX |  | 5 |  | 1000 |  | 30 | RET670 | Suitably Dimensioned |  | 177.3969
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
(OCEF Protection)
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
BC1 | Core3 |  | 1500 |  | 1 | 50 | 2.5 | 5P |  | 4 |  | 30 |  | - | REF615+REF615 | Suitably Dimensioned |  | 26.6667
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
(Low Imp. Busbar - 132kV side CT)
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
BC1 | Core5 |  | 3150 |  | 1 | 100 | 4 | PX |  | 10 |  | 3150 |  | 210.8 | REB500 | Suitably Dimensioned |  | 10
|  |  | 1500 | [6 empty] | 5 |  | 1000 |  | 147.73 |  | Suitably Dimensioned |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
(Hi Imp. REF - 132kV Side CT)
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
BC1 | Core2 |  | 1500 |  | 1 | 50 | 2.5 | PX |  | 3 |  | 1500 |  | 74.39 | RET615 | Suitably Dimensioned |  | 308.1917
|  |  | - | [6 empty] | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | -
T2N | Core1 |  | 1500 |  | 1 | 50 | 2.5 | PX |  | 10 |  | 1500 |  | 100 | RET615 | Suitably Dimensioned |  | 308.1917
|  |  | - | [6 empty] | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | -
0 | 0 |  | 1500 |  | 1 | 50 | 2.5 | PX |  | 3 |  | 1500 |  | 74.39 | RET615 | Suitably Dimensioned |  | 308.1917
|  |  | - | [6 empty] | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | -
(BCU)
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Burden (VA) |  |  | Connected Devices | CT Suitability
BC1 | Core4 |  | 1500 |  | 1 | 50 | 2.5 | 1FS5 |  | 20 |  | 20 |  | - | REC670 | Not suitable
|  |  | - | [6 empty] | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | -
(SBEF Protection - 132kV side CT)
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Burden (VA) |  |  | Connected Devices | CT Suitability |  | Required Vk (V)
T2N | Core2 |  | 1500 |  | 1 | 50 | 2.5 | 5P | 20 | 4 |  | 15 |  | - | REF615 | Suitably Dimensioned |  | 26.6667
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
Bus section coupler (BC1 - 13, 01,00, 10)
BUP - REF650,BCU - REC670
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Requried Kssc' |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Available Kssc' |  | Required Vk (V)
T1 | Core1 |  | 2500 |  | 1 | 120 | 6 | 5P20 |  | 5 |  | 20 |  | - | REF650 REC670 | Suitably Dimentioned |  | 114.4348 |  | 186.7176
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | - |  | #VALUE!
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
BBP FU2 - P743
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V) |  | Required Vk (V)
T1 | Core2 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 | P743 | Suitably Dimentioned |  | 123.5404 |  | 176.6733
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | - |  | 194.2823
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
BBP FU1 - REB500 BU
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V) |  | Required Vk (V)
T1 | Core3 |  | 2500 |  | 1 | 120 | 6 | PX - B |  | 5 |  | 750 |  | 60 | REB500 | Suitable Dimensions |  | 58.5314 |  | 10
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | - |  | 15.75
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
Transformer (BC2 - 11, 07,06)
HVC1 - REF650
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Required Kssc' |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Available Kssc' |  | Required Vk (V)
T1 | Core1 |  | 1250 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 | REF650 | Suitably Dimentioned |  | 126.2381 |  | 33.3333
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
HVC2 - MFAC+MVTP
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T1 | Core2 |  | 1250 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 | MFAC MVTP | Suitably Dimentioned |  | 468.3983
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
HVOC - REF650,HSOC - P141,POW,HV BCU - REC670,DFR - IDM+18,PQ100 - PM7500
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Requried Kssc' |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Available Kssc'
T1 | Core3 |  | 1250 |  | 1 | 120 | 6 | 5P20 |  | 5 |  | 40 |  | - | REF650 REC670 IDM+18 | Suitably Dimentioned |  | 112.6303
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
BBP FU1 - REB500 BU
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T1 | Core4 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 | REB500 | Suitable Dimensions |  | 58.5314
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
BBP FU2 - P743
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T1 | Core5 |  | 2500 |  | -1 | 120 | 6 | 0 |  | 5 |  | 750 |  | 60 | P743 | Suitably Dimentioned |  | 123.5404
|  |  | - | [6 empty] | 0 |  | 0 |  | 0 |  | 0 |  | -
|  |  | - | [6 empty] | 0 |  | 0 |  | 0 |  | 0 |  | -
Line Protection 400kV Feeder (BC3 - 09, 05, 04, 08)
IFP1 - RED670
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T1 | Core1 |  | 1000 |  | 1 | 120 | 6 | RED670 |  | 6 |  | 2000 |  | 30 | RED670 | Suitably Dimensioned |  | 829.9104
[10 empty] | - |  | - |  | - |  | - |  | -
[10 empty] | - |  | - |  | - |  | - |  | -
[10 empty] | Rct @ 75OC (Ω) |  | Rated Burden (VA) |  |  |  | CT Suitability |  | Required FS'
[10 empty] | 1 |  | 5 |  | - |  | Suitable Dimensions |  | 8.9954
[10 empty] | - |  | - |  | - |  | - |  | -
[10 empty] | - |  | - |  | - |  | - |  | -
[10 empty] | Rct @ 75OC (Ω) |  | Rated Burden VA |  | Im @ Vk (mA) |  | CT Suitability |  | Total Connected Burden | Effective Safety Factor of CT, FS'
[10 empty] | #REF! |  | #REF! |  | #REF! |  | #REF! |  | #REF! | #REF!
[10 empty] | #REF! |  | #REF! |  | #REF! |  | #REF! |  | #REF! | #REF!
[10 empty] | - |  | - |  | - |  | - |  | -
IFP2 - P545
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T1 | Core2 |  | 2500 |  | 1 | 120 | 6 | PX-A |  | 5 |  | 3750 |  | 60 | P545 | Suitably Dimensioned |  | 1560.8377
[10 empty] | - |  | - |  | - |  | - |  | -
[10 empty] | - |  | - |  | - |  | - |  | -
BUP - REF650,BCU - REC670,DFR/FL - IDM+9
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Required Kssc' |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Available Kssc'
T1 | Core3 |  | 2500 |  | 1 | 120 | 6 | 5P20 |  | 5 |  | 20 |  | - | REF650 REC670 IDM+9 | Suitably Dimentioned |  | 113.3599
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
GIB - REF650
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Required Kssc' |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Available Kssc'
T1 | Core4 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 20 |  | 60 | REF650 | Suitably Dimentioned |  | 126.2381
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
BBP FU1 - REB500 BU,BBP FU2 - P743
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T1 | Core5 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 | REB500 P743 | Suitable Dimensions |  | 59.4914
|  |  | - | [6 empty] | 5 |  | 750 |  | 60 |  | Suitably Dimentioned |  | 123.7404
|  |  | - | [6 empty] | 0 |  | 0 |  | 0 |  | 0 |  | -
COP1 MAIN
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Burden (VA) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required FS'
T1 | Core6 |  | 2500 |  | 1 | 120 | 6 | 0.2S |  | 5 |  | 10 |  | - | XC-RACK | Suitable Dimensions |  | 12.3253
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
COP1 CHECK
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Burden (VA) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required FS'
T1 | Core7 |  | 2000 |  | 1 | 120 | 6 | 0.2S |  | 5 |  | 10 |  | - | XC-RACK | Suitable Dimensions |  | 12.3253
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
CABLE CT GIB - REF650
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Required Kssc' |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Available Kssc'
T1 | Core1 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 20 |  | 60 | REF650 | Suitably Dimentioned |  | 126.2381
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
Line Protection HVDC Feeder (BC3 - 02, 03)
IFP1 - RED670
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T1 | Core1 |  | 2500 |  | 1 | 120 | 6 | PX-A |  | 5 |  | 3750 |  | 60 | RED670 | Suitably Dimensioned |  | 285.3205
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
IFP2 - P545
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T1 | Core2 |  | 2500 |  | 1 | 120 | 6 | PX-A |  | 5 |  | 3750 |  | 60 | P545 | Suitably Dimensioned |  | 585.3142
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | -
BUP - REF650,BCU - REC670,DFR/FL - IDM+9
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Required Kssc' |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Available Kssc'
T1 | Core3 |  | 2500 |  | 1 | 120 | 6 | 5P20 |  | 5 |  | 20 |  | - | REF650 REC670 IDM+9 | Suitably Dimentioned |  | 113.3599
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
BBP FU1 - REB500 BU
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T1 | Core4 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 | REB500 | Suitable Dimensions |  | 58.5314
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
BBP FU2 - P743
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required Vk (V)
T1 | Core5 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 | P743 | Suitably Dimentioned |  | 123.5404
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | -
METERING (CS1)
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Burden (VA) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required FS'
T1 | Core6 |  | 2000 |  | 1 | 120 | 6 | 0.2S |  | 5 |  | 10 |  | - | XC-RACK | Not suitable |  | 24.6507
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
METERING (CS2)
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Burden (VA) |  | Im @ Vk (mA) | Connected Devices | CT Suitability |  | Required FS'
T1 | Core7 |  | 2000 |  | 1 | 120 | 6 | 0.2S |  | 5 |  | 10 |  | - | XC-RACK | Not suitable |  | 24.6507
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  | - |  | -
VT parameters (Summary)
HVDC FEEDER
VT / Core |  |  |  | Voltage Ratio (kV) |  |  |  |  | VT Cable m/mm2 |  | Class |  | Rated Burden (VA) |  | VT Suitability |  |  | Required VA
T1 | Core1 |  |  | 400 | / √3 | / | 0.11 | / √3 | 120 | 6 | 0.5/3P |  | 50 |  | Suitably Dimensioned |  |  | 2.9515
| Core2 |  |  | 400 | / √3 | / | 0.11 | / √3 |  |  | 0.2 |  | 50 |  | Suitably Dimensioned |  |  | 2.7115
| Core3 |  |  | 400 | / √3 | / | 0.11 | / √3 |  |  | 0.2 |  | 50 |  | Suitably Dimensioned |  |  | 2.7115
FEEDER
VT / Core |  |  |  | Voltage Ratio (kV) |  |  |  |  | VT Cable m/mm2 |  | Class |  | Rated Burden (VA) |  | VT Suitability |  |  | Required VA
T1 | Core1 |  |  | 400 | / √3 | / | 0.11 | / √3 | 120 | 6 | 0.5/3P |  | 50 |  | Suitably Dimensioned |  |  | 2.9715
| Core2 |  |  | 400 | / √3 | / | 0.11 | / √3 |  |  | 0.2S |  | 50 |  | Suitably Dimensioned |  |  | 2.7115
|  | Core3 |  | 400 | / √3 | / | 0.11 | / √3 |  |  | 0.2S |  | 50 |  | Suitably Dimensioned |  |  | 2.7115
|  |  |  | Voltage Ratio (kV) | [6 empty] | Class |  | Rated Burden (VA) |  | VT Suitability |  |  | Required VA
|  | Core1 |  | 400 | / √3 | / | 0.11 | / √3 |  |  | 3P |  | 50 |  | Suitably Dimensioned |  |  | 2.9715
|  | - |  | - | 0 | - | - | 0 |  |  | - |  | - |  | - |  |  | 6.4615
| Core3 |  |  | 400 | / √3 | / | 0.11 | / √3 |  |  | 0.2S |  | 50 |  | Suitably Dimensioned |  |  | 2.7115
SGT | [19 empty] | Trafo Diff - 5P class
VT / Core |  |  |  | Voltage Ratio (kV) |  |  |  |  | VT Cable m/mm2 |  | Class |  | Rated Burden (VA) |  | VT Suitability |  |  | Required VA
T1 | Core1 |  |  | 400 | / √3 | / | 0.11 | / √3 | 120 | 6 | 3P |  | 50 |  | Suitably Dimensioned |  |  | 2.9715
| - |  |  | - |  | - | - |  |  |  | - |  | - |  | - |  |  | -
| - |  |  | - |  | - | - |  |  |  | - |  | - |  | - |  |  | -
(Transformer Differential - 33kV side CT)
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Burden (VA) |  |  | Connected Devices | CT Suitability |  | Calculated Vk (V) | Required Vk (V)

## CT ADEQUACY (hidden)
CT ADEQUACY CHECK
Back to
INDEX

## CT-VT Burdens
CT VT WIRING PARAMETERS CALCULATIONS
For CT Wiring
Burden of the connecting leads :
| Conductor cross section in mm2 | [5 empty] | A | = | 6 | mm2 | **
| Resistance in W/km at 200 C | [5 empty] | R20 | = | 3.69 | Ω/km |  |  | 7.41
| Specific resistance at 200 C |  | (copper wires) |  |  |  | a | = | 0.00393 | K-1
Resistance in Ω/km at t0 C = |  | R20 [ 1 + a ( t - 200 C ) ]
| Resistance in ohms/km at 750 C = | [6 empty] | = | 4.4876 | Ω/km |  |  | 4.4876 |  | 5.61
| Resistance in ohms/m at 750 C = | [5 empty] | R | = | 0.0044876 | Ω/m
| Secondary current of CT | [5 empty] | Is | = | 1 | A
| Relay Rated current | [5 empty] | Ir | = | 1 | A
| Conductor length in meters ( CT to relay ) | [5 empty] | l | = | 120 | m | **
| Lead Resistance from the CT to Relay | [5 empty] | RL =R x l | = | 0.53851 | Ω
| Lead Resistance of the current loop from the CT to Relay | [5 empty] | 2RL = 2 x R x l | = | 1.077 | Ω |  |  | 1.077 |  | 1.077
| VA consumption of the connecting leads | [5 empty] | Pl = Is2 x Rl | = | 1.077 | VA |  |  | 1.077
| 165m Lead Resistance of the current loop from the 33kV Incomer SWGR to 220kV Transformer Protection Panel. | [7 empty] | 0.74045 | VA
For VT Wiring
Burden of the connecting leads :
| Conductor cross section in mm2 | [5 empty] | A | = | 2.5 | mm2 | **
| Resistance in W/km at 200 C | [5 empty] | R20 | = | 7.41 | Ω/km
| Specific resistance at 200 C |  | (copper wires) |  |  |  | a | = | 0.00393 | K-1
Resistance in Ω/km at t0 C = |  |  | R20 [ 1 + a ( t - 200 C ) ]
| Resistance in W/km at 750 C = | [6 empty] | = | 9.0117 | Ω/km
| Resistance in W/m at 750 C = | [5 empty] | R | = | 0.0090117 | Ω/m
| Primary Voltage of VT | [5 empty] | Vp | = | 400 / √3 | kV
| Secondary Voltage of VT | [5 empty] | Vs | = | 0.11 / √3 | kV
| Conductor length in meters ( VT to relay ) | [5 empty] | l | = | 150 | m | **
| Lead Resistance from the VT to Relay | [5 empty] | RL =R x l | = | 1.3518 | Ω
| Lead Resistance of the current loop from the VT to Relay | [5 empty] | 2RL = 2 x R x l | = | 2.7035 | Ω
|  |  | ** | Assumed
CT/VT Burden of Connected Devices (per phase): | [6 empty] | CT at 1A |  | VT at 110V |  |  | Note: Pl. refer the manual for CT/VT burden at different rated currents and voltages
| Relion 670/650 series Relays |  |  |  |  | IED 670/650 | 0.02 |  | 0.02 | VA |  |  | 150mVA for 5A |  |  | 0.006
| Busbar Protection Relay |  |  |  |  | REB500 | 0.01 |  | 0.15 | VA
| ABB REx 52x Relays |  |  |  |  | REJ525/REJ521/REX521 | 0.1 |  | 0.5 | VA
| ABB Relion 650 series Relays |  |  |  |  | IED650 | 0.02 |  | 0.02 | VA
| ABB SPACOM Relays |  |  |  |  | SPAJ/SPAU/SPAF 1xxC series | 0.1 |  | 0.5 | VA
| ABB REx54x series Relays |  |  |  |  | REF54x/RET54x | 0.02 |  | 0.5 | VA
| ABB Relion 630/620 series Relays |  |  |  |  | IED630/620 | 0.02 |  | 0.05 | VA
| ABB Relion 615 series Relays |  |  |  |  | IED615 | 0.02 |  | 0.05 | VA
| ABB REU523 Relay |  |  |  |  | REU523 | - |  | 0.1 | VA
| FMS |  |  |  |  | Indactic 650 | 0.2 |  |  | VA
| TOSHIBA Line Diff. Relay |  |  |  |  | GRL 100 | 0.1 |  | 0.1 | VA
| TOSHIBA Line Dist. Relay |  |  |  |  | GRZ 101 | 0.1 |  | 0.1 | VA
| SIEMENS Line Distance Protection |  |  |  |  | 7SA52xx | 0.1 |  | 0.1 | VA
| SIEMENS Siprotec Relay |  |  |  |  | 7SD522/7SL86 | 0.05 |  | 0.1 | VA
| SIEMENS Transformer Protection Relay |  |  |  |  | 7UT85 | 0.1 |  | 0.1 | VA |  |  |  | 7UT633/635
| AVR Relay |  |  |  |  | Tapcon260 | - |  | 1 | VA
| SIEMENS BFR + O/C relay |  |  |  |  | 7SJ6144 | 0.05 |  | - | VA
| SIEMENS Pilot wire prot. relay |  |  |  |  | SOLKAR RF / N | 0.05 |  | - | VA
| SIEMENS Low Imp. Busbar prot. relay |  |  |  |  | 7SS5xx | 0.1 |  | - | VA
| AREVA Low Imp. Busbar prot. Relay |  |  |  |  | P74x | 0.04 |  | - | VA
| AREVA P63_ Tr. Diff. Relay |  |  |  |  | P63x | 0.1 |  | 0.3 | VA
| AREVA High Imp. Busbar prot. relay |  |  |  |  | MCAG3x | 1 |  | - | VA
| AREVA CT sup. Relay |  |  |  |  | MVTP31 | 0.002 |  | - | VA
| AREVA Line Differential+Distance+DEF Protection |  |  |  |  | P54x | 0.15 |  | 0.02 | VA
| Siemens High Impedance Busbar Protection |  |  |  |  | DAD | 0.1 |  | - | VA
| SEL Transformer Differential Relay |  |  |  |  | SEL487E | 0.1 |  | 0.1
| SIEMENS Relay |  |  |  |  | 7SJ8 | 0.1 |  | 0.1 | VA
| SEL 751 |  |  |  |  | SEL751 | 0.01 |  | 0.1 | VA
| SEL Transformer Differential Relay 478E |  |  |  |  | SEL 487E | 0.1 |  | 0.1 | VA
| SEL Generator Prot. Relay |  |  |  |  | SEL700G | 0.01 |  | 0.1 | VA
| Synchroscope (SQ0214) | [7 empty] | 4 | VA
| Paralleling Device (7VE6110) | [7 empty] | 0.3 | VA
| Auto Synchroniser (7VE6110) | [7 empty] | 0.3 | VA
| MFM | [5 empty] | 0.1 |  | 0.1 | VA
| SEL Line Differential Relay 411L |  |  |  | SEL411L |  | 0.13 |  | 0.13 | VA
| Tariff Meter |  |  |  |  | XC-RACK | 0.008 |  | 2.7 | VA
| Ammeter |  |  |  |  | GOSSEN | 0.25 |  |  | VA
| AVR Relay |  |  |  |  | ZIV | 0.2 |  | 0.1 | VA
| Analog Ammeter/Voltmeter/Watt meter/VAR meter | [5 empty] | 0.1 |  | 0.1 | VA | **
| Dual Voltmeter/ Dual Frequency Meter | [7 empty] | 2.3 | VA
| Tariff Meter ( Main and Check) |  |  |  |  | Prometer 100 | 0.1 |  | 0.1 | VA
| FMS |  |  |  |  | IDM+ | 0.058 |  | 0.378 | VA | [5 empty] | For 1A | For 5A
| ZIV AVR Relay |  |  |  |  | RTF | 0.2 | [5 empty] | (0.2 VA) / (I2n2) |  |  | 0.2 | 0.008
# Refer Annexure-A for the Relays and Auxiliary Components burdens
** Assumed
| Voltmeter |  |  |  |  | Pointer |  |  | 3.75 | VA
| Ammeter |  |  |  |  | Pointer | 1.25 |  |  | VA
| BBP |  |  |  | P741/3 |  | 0.1
| IFP |  |  |  | P545 |  | 0.02
| HSOC |  |  |  | P141 |  | 0.04
Back to
INDEX
Note on S10: aeprcha: Usually 4.00 sqmm Sometimes 6.00 sqmm
Note on S11: aeprcha: 4.20 for 4 sqmm cable 2.80 for 6 sqmm cable
Note on S12: Praful Chandarana: usually 0.00393
Note on S28: aeprcha: Usually 4.00 sqmm Sometimes 6.00 sqmm
Note on S29: aeprcha: 4.20 for 4 sqmm cable 2.80 for 6 sqmm cable

## Parameters & Fault Cal. (4)
System Parameters & Fault Current Cal.
System Parameters:
|  | System Frequency | [13 empty] | 50 |  | Hz
|  | Bus Voltage Level | [13 empty] | 132 |  | kV
|  | Max. Bus fault level | [13 empty] | 50 |  | kA
|  | X/R Ratio | [13 empty] | 40 |  |  |  | As per Transco spec page 7/34
|  | MV Bus Voltage Level | [13 empty] | 132 |  | kV
|  | MV Max. Bus fault level/Switchgear Rating | [13 empty] | 40 |  | kA |  | As pre SLD
LV X/R Ratio
Power line parameters:
Assumed Cable: |  |  |  | 3 | C, | CU | HDPE, |  | 240 |  | mm2, |  | 1 | Cables/phase
Cable Details
|  | Positive Sequence- Resistance | [11 empty] | R1 | = | 0.0222 |  | Ω/Km
|  | Positive Sequence- Reactance | [11 empty] | X1 | = | 0.17 |  | Ω/Km
|  | Zero Sequence- Resistance | [11 empty] | R0 | = | 0.14 |  | Ω/Km
|  | Zero Sequence- Reactance | [11 empty] | X0 | = | 0.07 |  | Ω/Km
|  | Route length | [12 empty] | = | 0.4 |  | km
|  | Cable +Ve seq. impedence | [6 empty] | Z1 | = | 0.0222 |  | + j | 0.17 |  | Ω/Km
|  | Cable Zero seq. impedence | [6 empty] | Z0 | = | 0.14 |  | + j | 0.07 |  | Ω/Km
|  | Total cable +Ve seq. impedence | [6 empty] | Z1L | = | 0.00888 |  | + j | 0.068 |  | Ω
|  | Total cable Zero seq. impedence | [6 empty] | Z0L | = | 0.056 |  | + j | 0.028 |  | Ω
Fault Current & Time Constant Calculations:
|  | Maximum HV Busbar fault current | [12 empty] | = | 50000 |  | A
|  | HV rating of Busbar | [12 empty] | = | 132000 |  | V
|  | Maximum MV Busbar fault current | [12 empty] | = | 40000 |  | A
|  | MV rating of Busbar | [12 empty] | = | 132000 |  | V
For the above fault condition Source impedance (Zs), considering voltage | [14 empty] | = | 1 |  | pu
|  |  |  | Zs | = | (V | X | 1 | ) / | (√3 | x | I) |  |  | = | 1.5242 |  | Ω
|  |  |  | Source X / R ratio | = | 2 | x | p | x | f | x | (L/R)
|  |  |  | System X/R Ratio | [6 empty] | X/R |  |  |  | = | 40
|  |  |  | System Frequency | [6 empty] | f |  |  |  | = | 50
|  | Now, |  | Impedence Angle | [6 empty] | øs = | Tan-1(X/R)
|  |  |  | Impedence Angle in radians | [6 empty] | øs |  |  |  | = | 1.5458
|  |  |  | Impedence Angle in Degrees | [6 empty] | øs |  |  |  | = | 88.5679
|  |  |  | System Resistance | [5 empty] | Rs | =Zs x Cos øs |  |  |  | = | 0.038093 |  | W
|  |  |  | System Reactance | [5 empty] | Xs | =Zs x Sin øs |  |  |  | = | 1.5237 |  | W
|  | Hence, |  | Source Impedence | [5 empty] | Zs | = |  | 0.038093 |  | + j | 1.5237 |  | W
Source Impedance Ratio (SIR)
|  | SIR | = | Zs | / | (80% * Z1L) |  |  |  |  | where, |  | Z1L | = | 0.068577 |  | ohm
|  |  | = | 1.5242 |  | / | ( 0.8 * |  | 0.068577 |  | )
|  |  | = | 27.7826
Determination of System Time-constant (L/R):
| Source X / R ratio |  |  |  |  | = | 2 | x | p | x | f | x | (L/R)
| System X/R Ratio | [12 empty] | X/R | = | 40
| System Frequency | [12 empty] | f | = | 50 |  | Hz
| Hence, System tp (L/R) |  |  |  |  | = | X/R | / | 2 | x | p | x | f |  | = | 127.2727 |  | ms
Determination of Fault Current for 3-ph Through Fault:
Fault Impedence |  |  |  | Z1t | = |  | Zs | + | Z1L
[5 empty] | = ( | 0.038093 |  | + j | 1.5237 |  | ) + ( | 0.00888 |  | + j | 0.068 |  | )
[5 empty] | = | 0.046973 |  | +j | 1.5917 |  | W
[5 empty] | = | 1.5924 |  | Ð | 88.3096 |  | W
|  |  |  | Therefore, X/R ratio | = | 33.8859
| Hence, 3-ph fault current for Through faults | [9 empty] | = | 132000 |  | x | 1
[12 empty] | 1.5924 |  | x | √3 | 1.7321
[11 empty] | = | 47858.0776 |  | A
Determination of Time-constant for 3-ph Through fault (L/R):
| X / R ratio |  |  |  |  | = | 2 | x | p | x | f | x | (L/R)
| X/R Ratio for 3-ph Through Fault | [12 empty] | X/R | = | 33.8859
| System Frequency | [12 empty] | f | = | 50 |  | Hz
| Hence, System tp (L/R) |  |  |  |  | = | X/R | / | 2 | x | p | x | f |  | = | 107.8187 |  | ms
Determination of 1-ph to Earth Through fault
Cable Impedence |  |  |  | Zot | = |  | Zs | + | Z0L
[5 empty] | = ( | 0.038093 |  | + j | 1.5237 |  | ) + ( | 0.056 |  | + j | 0.028 |  | )
[5 empty] | = | 0.094093 |  | +j | 1.5517 |  | W
[5 empty] | = | 1.5546 |  | Ð | 86.53 |  | W
Fault Impedence |  |  |  | Z0f | = |  | Z1t | + | Z2t | + | Zot
| = ( | 0.046973 |  | +j | 1.5917 |  | ) + ( | 0.046973 |  | +j | 1.5917 |  | ) + ( | 0.094093 |  | +j | 1.5517 |  | )
| = | 0.18804 |  | +j | 4.7352
| = | 4.7389 |  | Ð | 87.7259 |  | W | [5 empty] | Therefore, X/R ratio | = | 25.1818
| Hence, 1-ph fault current for Through faults | [9 empty] | = | 132000 |  | x | 1 |  | x | 3
[12 empty] | 4.7389 |  | x | √3 | 1.7321
[11 empty] | = | 48245.339 |  | A
Determination of Time-constant for 1-ph to earth Through fault (L/R):
| X / R ratio |  |  |  |  | = | 2 | x | p | x | f | x | (L/R)
| X/R Ratio for 1-ph to Earth Through Fault | [12 empty] | X/R | = | 25.1818
| System Frequency | [12 empty] | f | = | 50 |  | Hz
| Hence, System tp (L/R) |  |  |  |  | = | X/R | / | 2 | x | p | x | f |  | = | 80.1241 |  | ms
Calculation of 3-ph fault current Endzone-1 (80%)
Fault Impedence |  |  |  | Z1zone-1 | = |  | Zs | + | (0.8 | x | Z1L)
[5 empty] | = ( | 0.038093 |  | + j | 1.5237 |  | ) + | 0.8 | x ( | 0.00888 |  | + j | 0.068 |  | )
[5 empty] | = | 0.045197 |  | +j | 1.5781 |  | W
[5 empty] | = | 1.5788 |  | Ð | 88.3595 |  | W
|  |  |  | Therefore, X/R ratio | = | 34.9165
| Hence, 3-ph fault current for Endzone-1 faults | [9 empty] | = | 132000 |  | x | 1
[12 empty] | 1.5788 |  | x | √3 | 1.7321
[11 empty] | = | 48271.7306 |  | A
Determination of Time-constant for 3-ph Fault Endzone-1 (L/R):
| X / R ratio |  |  |  |  | = | 2 | x | p | x | f | x | (L/R)
| X/R Ratio for 3-ph Fault Endzone-1 | [12 empty] | X/R | = | 34.9165
| System Frequency | [12 empty] | f | = | 50 |  | Hz
| Hence, System tp (L/R) |  |  |  |  | = | X/R | / | 2 | x | p | x | f |  | = | 111.098 |  | ms
Calculation of 1-ph to earth fault current EndZone-1 (80%)
Cable Impedence |  |  |  | Zozone-1 | = |  | Zs | + | (0.8 | * | Z0L)
[5 empty] | = ( | 0.038093 |  | + j | 1.5237 |  | ) + | 0.8 | x ( | 0.056 |  | + j | 0.028 |  | )
[5 empty] | = | 0.082893 |  | +j | 1.5461 |  | W
[5 empty] | = | 1.5483 |  | Ð | 86.9311 |  | W
Fault Impedence |  |  |  | Z0fzone-1 | = | Z1zone-1 |  | + | Z2zone-1 |  | + | Zozone-1
| = ( | 0.045197 |  | +j | 1.5781 |  | ) + ( | 0.045197 |  | +j | 1.5781 |  | ) + ( | 0.082893 |  | +j | 1.5461 |  | )
| = | 0.17329 |  | +j | 4.7024
| = | 4.7056 |  | Ð | 87.8895 |  | W
[10 empty] | Therefore, X/R ratio | = | 27.1363
| Hence, 1-ph to earth Fault current for Endzone-1 | [9 empty] | = | 132000 |  | x | 1 |  | x | 3
[12 empty] | 4.7056 |  | x | √3 | 1.7321
[11 empty] | = | 48587.1707 |  | A
Determination of Time-constant for 1-ph to earth Fault Endzone-1 (L/R):
| X / R ratio |  |  |  |  | = | 2 | x | p | x | f | x | (L/R)
| X/R Ratio for 3-ph Through Fault | [12 empty] | X/R | = | 27.1363
| System Frequency | [12 empty] | f | = | 50 |  | Hz
| Hence, System tp (L/R) |  |  |  |  | = | X/R | / | 2 | x | p | x | f |  | = | 86.3428 |  | ms
Back to
INDEX
Note on Q11: aeprcha: (400kV-60, 220kV to 132kV-40, below 132 kV-15, usually)
Note on Q14: aeprcha: (400kV-60, 220kV to 132kV-40, below 132 kV-15, usually)
Note on Q37: aeprcha: Usually 1.0 or 1.1

## BAY1 (hidden)
Bus section coupler (BC1 - 13, 01,00, 10)
Back to
INDEX

## BUP BCU (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | BUS SECTION COUPLER | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core1 |  |  |  | (OC+BCPU+FMS) | [10 empty] | Connected devices: | REC670
REF650
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | 5P20
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [11 empty] | #REF!
| Magnetizing Current: |  |  |  |  | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 5 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.117 |  | VA
Non-directional instantaneous and definitive time, phase and residual overcurrent protection
| Ealreq = |  |  | 1.5 | x | Iop | Isr |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[7 empty] | Ipr | [7 empty] | Ir | x | Ir
6 times rated primary current concidered
|  | The primary operate value (A) | [13 empty] | Iop | = | 15000 |  | A
|  | The rated primary CT current (A) | [13 empty] | Ipr | = | 2500 |  | A
|  | The rated secondary CT current (A) | [13 empty] | Isr | = | 1 |  | A
|  | The rated current of the protection IED (A) | [13 empty] | Ir | = | 1 |  | A
|  | The secondary resistance of the CT (ohm) | [13 empty] | Rct | = | 5 |  | ohm
|  | The resistance of the secondary cable and additional load (ohm). | [13 empty] | RL | = | 1.117 |  | ohm
|  | The burden of an IED current input channel (VA) | [13 empty] | SR | = | 0.02 |  | VA
| Ealreq = |  | 1.5 | x | 15000 |  | x | 1 |  | x | ( | 5 | + | 1.117 | + | 0.02 |  |  | )
[8 empty] | 2500 | [7 empty] | 1 | x | 1
|  | = | 55.24 |  | V
Non-directional inverse time delayed phase and residual overcurrentprotection
| Ealreq = |  |  | 20 | x | Iop | Isr |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[7 empty] | Ipr | [7 empty] | Ir | x | Ir
1.2 times rated primary current concidered
|  | The primary operate value (A) | [13 empty] | Iop | = | 3000 |  | A
|  | The rated primary CT current (A) | [13 empty] | Ipr | = | 2500 |  | A
|  | The rated secondary CT current (A) | [13 empty] | Isr | = | 1 |  | A
|  | The rated current of the protection IED (A) | [13 empty] | Ir | = | 1 |  | A
|  | The secondary resistance of the CT (ohm) | [13 empty] | Rct | = | 5 |  | ohm
|  | The resistance of the secondary cable and additional load (ohm). | [13 empty] | RL | = | 1.117 |  | ohm
|  | The burden of an IED current input channel (VA) | [13 empty] | SR | = | 0.02 |  | VA
| Ealreq = |  | 20 | x | 3000 |  | x | 1 |  | x | ( | 5 | + | 1.117 | + | 0.02 |  |  | )
[8 empty] | 2500 | [7 empty] | 1 | x | 1
|  | = | 147.29 |  | V
|  |  | KPV as per Hitachi recommendation | [7 empty] | Eal | ≥ | max(55.24,147.29) | [8 empty] | ( | max | , | )
[11 empty] | Eal | ≥ | 147.29
[11 empty] | 750 | ≥ | 147.29
[5 empty] | Hence CT is: |  | Suitably Dimensioned
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | CT Resistance (W) @ 75OC |  | Limiting Secondary Voltage (Ual), V |  | Mag. Current (Io), mA at Vk |  | Relay / Instrument Type |  | CT Suitability
T1 | Core1 |  | 2500 |  | 1 | 120 | 6 | 5P20 |  | 5 |  | 750 |  | 50 |  | REC670+REF650+ |  | Suitably Dimensioned
|  |  | - | [6 empty] | - |  | - |  | - |  |  |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  |  |  | -

## BUP BCU(1) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AK | Checked By |  |  | LN | BUS SECTION COUPLER | [6 empty] | Contractor |  |  | HITACHI ENERGY
| T1 |  | Core1 | [14 empty] | Connected devices: | REF650
REC670
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | 5P20
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> |  |  | V | [11 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead + other burden | [5 empty] | PL | = | 1.117 |  | VA |  |  | = | 5 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula: | [20 empty] | The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2500 |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 0 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 5 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.117 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN | = | 30
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | 0 |  | x | 1 | ) / | 20 | ) - | 5
|  |  | = | -5 |  | VA
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 50000 |  | / | 2500
[5 empty] | = | 20
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 5 | + | 30 | ) / ( | 5 | + | 1.117 | )
[5 empty] | = | 114.4348
|  |  |  | Available Kssc' | = =: >; 20 n: Required Kssc'
|  |  | 114.4348 |  | = =: >; 20 n: 20
|  |  |  | Hence CT is: | 20 n: Suitably Dimentioned
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  | 20 n: CT Cable m/mm2; 20 PE: Class; 20 PN: CT Resistance (W) @ 75OC; 20 PE: Required Kssc'; 20 PL: Avilable Kssc' | Relay / Instrument Type |  | CT Suitability
T1 | Core1 |  | 2500 |  | 1 | 120 | 6 | 5P20 | #REF! | 5 |  | 20 |  | 114.4348 |  | REF650 REC670 |  | Suitably Dimentioned
|  |  | - | [14 empty] | - | bar: 20 PN; 20 PE; 20 PL
|  |  | - | [14 empty] | - | bar: 20 PN; 20 PE; 20 PL

## BBP P743(1) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | BUS SECTION COUPLER | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core2 | [14 empty] | Connected devices: | P743
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [12 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.177 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 50000 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 2500 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | 20 |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 1.177 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 50000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | 20 |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | 20 |  | x ( | 5 |  | + | 1.177 |  | )
|  |  | = | 61.7702
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 20 |  | x ( | 5 |  | + | 1.177 |  | )
|  |  | = | 123.5404
Adequacy Check
Criteria I
[5 empty] | Available Vk | > | Required Vk |  |  |  | (Criteria I)
|  |  |  | 750 |  | > | 61.7702
[5 empty] | Hence: |  | Criteria I |  | is | Satisfied
Criteria II
[5 empty] | Available Vk | > | Required Vk |  |  |  | (Criteria II)
|  |  |  | 750 |  | > | 123.5404
[5 empty] | Hence: |  | Criteria II |  | is | Satisfied
[5 empty] | Hence CT is: |  | Suitably Dimentioned
| T1 |  | Core2 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | P743
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [7 empty] | PX-B
| CT Resistance: | [6 empty] | Rct< |  |  | W
| Knee Point Voltage: | [6 empty] | Vk> |  |  | V | [10 empty] | Under Dimentioned
| Magnetizing Current: | [6 empty] | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.177 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 50000 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 2500 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | 20 |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 1.177 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 50000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | 20 |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | 20 |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | 11.7702
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 20 |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | 23.5404
Adequacy Check
Criteria I
[5 empty] | Available Vk | < | Required Vk |  |  |  | (Criteria I)
|  |  |  | 0 |  | < | 11.7702
[5 empty] | Hence: |  | Criteria I |  | is | Not Satisfied
Criteria II
[5 empty] | Available Vk | < | Required Vk |  |  |  | (Criteria II)
|  |  |  | 0 |  | < | 23.5404
[5 empty] | Hence: |  | Criteria II |  | is | Not Satisfied
[5 empty] | Hence CT is: |  | Under Dimentioned
ABB
| T1 |  | Core2 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | P743
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [9 empty] | PX-B
| CT Resistance: | [8 empty] | Rct< |  |  | W
| Knee Point Voltage: | [8 empty] | Vk> |  |  | V | [8 empty] | #VALUE!
| Magnetizing Current: | [8 empty] | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.177 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 50000 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | - |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | #VALUE! |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 1.177 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 50000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | #VALUE! |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | #VALUE! |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | #VALUE!
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | #VALUE! |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | #VALUE!
ABB
Adequacy Check
Criteria I
[5 empty] | Available Vk | #VALUE! | Required Vk |  |  |  | (Criteria I)
|  |  |  | 0 |  | #VALUE! | #VALUE!
[5 empty] | Hence: |  | Criteria I |  | is | #VALUE!
Criteria II
[5 empty] | Available Vk | #VALUE! | Required Vk |  |  |  | (Criteria II)
|  |  |  | 0 |  | #VALUE! | #VALUE!
[5 empty] | Hence: |  | Criteria II |  | is | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
ABB
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | CT Resistance (W) @ 75OC |  | Limiting Secondary Voltage (Ual), V |  | Mag. Current (Io), mA at Vk |  | Relay / Instrument Type |  | CT Suitability
T1 | Core2 |  | 2500 |  | 1 | 120 | 6 | PX-B | #REF! | 5 |  | 750 |  | 60 |  | P743 |  | Suitably Dimentioned
|  |  | - | [6 empty] | - |  | - |  | - |  |  |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  |  |  | -

## BBP FU1 - REB500 (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | BUS SECTION COUPLER | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core3 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | REB500
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX - B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [12 empty] | #REF!
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 5 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.087 |  | VA
CT-Requirements for BB Protection
|  | Maximum Primary Fault Current | [13 empty] | Isc | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2500 |  | A
|  | Rated Voltage | [13 empty] | UN2 | = | 400 |  | kV
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 750 |  | V
|  | Internal Resistance CT | [13 empty] | Rct | = | 5 |  | VA
|  | Conn. Lead + Relay Burden | [13 empty] | RL | = | 1.087 |  | VA
|  | Rated Secondary Current, | [13 empty] | Isc | = | 1 |  | A
|  | Nominal Frequency of the network | [13 empty] | fn | = | 50
Required OC factor condition. 1:
At Max. Through fault current CT’s shall not saturate for currents below 5 times rated current.
[8 empty] | n' | = | Isc
5 * Ipn
Required OC factor Condition 2:
n2' >= 10 for TN <=120 msec
n2' >= 20 for 120ms <= TN <=300 ms
| Where, |  | n' = Required OC factor
Isc = max. bus fault current
Ipn = Rated primary current (A)
[23 empty] | ** | Rated Bus fault current
Required OC factor condition 1:
|  | n'(1) | = | 50000
5 x 2500
|  | n'(1) | = | 4
Required OC factor condition 2:
|  |  |  | TN = | 1 |  | X | X
[6 empty] | 2* ϖ* fn |  | R
[5 empty] | 1 |  |  |  | x | 15
|  |  | TN | = | 2 * 3.14 * 50
|  |  |  | = | 0.047771 |  | sec
|  |  | TN | = | 47.7707 |  | ms
| Hence n'(2) 10 |  |  | = | 10
Required OC factor n' >= max( n'(1) ; n'(2))
n' >=max(4 ; 10)
Therefore
|  | n' | = | 10 |  | Necessary Condition
Required secondary equivalent limiting secondary e.m.f
Eal >= n' *(RCT+RL+Rr)*Isn
| = | 10 | x | ( | 5 |  | + | 1.087 | + | 0.01 | ) | x | 1
| Eal | = | 60.9702 | V
| According to IEC 61869 class PX | [7 empty] | Eknee |  | > |  | 0.8*Eal
[11 empty] | = |  | 48.7762
[5 empty] | With design margin 120% | [5 empty] | = |  | 58.5314
[10 empty] | Available Vk | > | Required Vk
[8 empty] | 750 |  |  | > | 58.5314
[10 empty] | Hence CT is: |  | Suitable Dimensions
| T1 |  | Core3 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | REB500
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [7 empty] | PX - B
| CT Resistance: | [6 empty] | Rct< | 9.3 |  | W
| Knee Point Voltage: | [6 empty] | Vk> | 500 |  | V | [10 empty] | Required Vk
| Magnetizing Current: | [6 empty] | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 9.3
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 9.3 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.087 |  | VA
CT-Requirements for BB Protection
|  | Maximum Primary Fault Current | [13 empty] | Isc | = | 31500 |  | A | **
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Voltage | [13 empty] | UN2 | = | 33 |  | kV
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 500 |  | V
|  | Internal Resistance CT | [13 empty] | Rct | = | 9.3 |  | VA
|  | Conn. Lead + Relay Burden | [13 empty] | RL | = | 1.087 |  | VA
|  | Rated Secondary Current, | [13 empty] | Isc | = | 1 |  | A
|  | Nominal Frequency of the network | [13 empty] | fn | = | 50
Required OC factor condition. 1:
At Max. Through fault current CT’s shall not saturate for currents below 5 times rated current.
[8 empty] | n' | = | Isc
5 * Ipn
Required OC factor Condition 2:
n2' >= 10 for TN <=120 msec
n2' >= 20 for 120ms <= TN <=300 ms
Where,
n' = Required OC factor
Isc = max. bus fault current
Ipn = Rated primary current (A)
[10 empty] | ** | Rated Bus fault current
Required OC factor condition 1:
|  | n'(1) | = | 31500
5 x -
|  | n'(1) | = | #VALUE!
Required OC factor condition 2:
|  |  |  | TN = | 1 |  | X | X
[6 empty] | 2* ϖ* fn |  | R
| As per Transco Standard for 33kV system X/R | [11 empty] | = | #REF!
[5 empty] | 1 |  |  |  | x | #REF!
|  |  | TN | = | 2 * 3.14 * 50
|  |  |  | = | #REF! |  | sec
|  |  | TN | = | #REF! |  | ms
| Hence n'(2) 10 |  |  | = | 10
Required OC factor n' >= max( n'(1) ; n'(2))
n' >=max(3.15 ; 10)
Therefore
|  | n' | = | #VALUE! |  | Necessary Condition
Required secondary equivalent limiting secondary e.m.f
Eal >= n' *(RCT+RL+Rr)*Isn
| = | #VALUE! | x | ( | 9.3 |  | + | 1.087 | + | 0.01 | ) | x | 1
| Eal | = | #VALUE! | V
| According to IEC 61869 class PX | [7 empty] | Eknee |  | > |  | 0.8*Eal
[11 empty] | = |  | #VALUE!
[5 empty] | With design margin 120% | [5 empty] | = |  | #VALUE!
[10 empty] | Available Vk | #VALUE! | Required Vk
[9 empty] | 500 |  | #VALUE! | #VALUE!
[10 empty] | Hence CT is: |  | #VALUE!
| T1 |  | Core3 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | REB500
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [9 empty] | PX - B
| CT Resistance: | [8 empty] | Rct< | - |  | W
| Knee Point Voltage: | [8 empty] | Vk> | - |  | V | [8 empty] | #VALUE!
| Magnetizing Current: | [8 empty] | I0< | - |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | #VALUE! |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.087 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 1 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | - |  | V
|  | Internal Burden, | [13 empty] | PE | = | #VALUE! |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.087 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | - |  | x | 1 | ) / | 20 | ) - | #VALUE!
|  |  | = | #VALUE! |  | VA
The CT requirement is as follows:
where
| n' | ³ | n1 |  | --- (i) |  |  |  |  | n' | = | The effective accuracy limiting factor
| n' | ³ | n2 |  | --- (ii) | [5 empty] | = | n x (PN + PE) / (PL + PE)
[10 empty] | n1 | = | Itkmax / (5 x Ipn)
[10 empty] | n2 | = | 10 |  | ...for | TP | £ | 120 | msec
[11 empty] | = | 20 |  | ...for | TP | £ | 300 | msec
Calculation for n1: | [9 empty] | n1 | = | Itmax |  | / ( | 5 | x | Ipn |  | )
[11 empty] | = | 1 |  | / ( | 5 | x | - |  | )
[11 empty] | = | #VALUE!
Calculation for n2: |  |  |  | Since Tp |  | = | #REF! |  | , | n2 | = | #REF!
Calculation for n': | [5 empty] | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[6 empty] | = | 20 | x ( ( | #VALUE! | + | #VALUE! | ) / ( | #VALUE! | + | 1.087 | )
[6 empty] | = | #VALUE!
Checking the conditions ---(i) and ---(ii) mentioned aove:
|  |  | #VALUE! |  | #VALUE! | =: #VALUE!; PE: --- (i)
|  |  | #VALUE! |  | #VALUE! | =: #REF!; PE: --- (ii)
|  |  |  | Hence CT is: |  | =: #VALUE!
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | =: CT Cable m/mm2; x ( (: Class; +: CT Resistance (W) @ 75OC; ) / (: Limiting Secondary Voltage (Ual), V; +: Mag. Current (Io), mA at Vk; ): Relay / Instrument Type |  | CT Suitability
T1 | Core3 |  | 2500 |  | 1 | 120 | 6 | PX - B | #REF! | 5 |  | 750 |  | 60 |  | REB500 |  | Suitable Dimensions
|  |  | - | [14 empty] | - | bar: +; ) / (; +
|  |  | - | [14 empty] | - | bar: +; ) / (; +

## IFP1-RED670
RED670 TEMPLATE.
Here We have placed the calculations CT Adequacy Check of Two tapping for RED 670
| T1 |  | Core1 |  |  |  | (Diff. + Dist.) | [10 empty] | Connected devices: | RED670 |  | Note: CT requirements for other protection functions are different. Pl. refer to Application Manual
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 1000 |  | 1500 |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-A
| CT Resistance: |  |  |  |  | Rct < | 6 |  | W
| Knee Point Voltage: |  |  |  |  | Vk > | 2000 |  | V | [11 empty] | Highest Vk required = |  | 829.9104
| Magnetizing Current: |  |  |  |  | I0< | 30 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | RED670 |  |  |  | Sr' | = | 0.02 |  | VA |  | Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Burden of | [6 empty] | = |  |  | VA |  |  | = | 1.097 | / ( | 1 | x | 1 | )
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  | Lead + Other resisitance connected =: =; Lead + Other resisitance connected Sl: 1.097; Lead + Other resisitance connected Isn: W
| Total lead + other burden | [5 empty] | Sl | = | 1.097 |  | VA
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer.
For Close-in faults:
Ealreq = |  |  |  |  | Ikmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
For Through faults:
Ealreq = |  |  | 2 | x | Itmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
| Equivalent Secondary emf. Required | [11 empty] | Lead + Other resisitance connected Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Lead + Other resisitance connected Sl: Ipn; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 1000; Lead + Other resisitance connected Isn: A
| Max. primary fundamental frequency fault current for close-in faults | [11 empty] | Lead + Other resisitance connected Sl: Ikmax; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 50000; Lead + Other resisitance connected Isn: A
| Max. primary fundamental frequency fault current for through fault | [13 empty] | Itmax | = | 47858.0776 |  | A | 3-phase
[16 empty] | = | 48245.339 |  | A | 1-phase
| CT secondary rated current | [11 empty] | Lead + Other resisitance connected Sl: Isn; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 1; Lead + Other resisitance connected Isn: A
| Relay rated current | [11 empty] | Lead + Other resisitance connected Sl: Ir; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 1; Lead + Other resisitance connected Isn: A
| CT secondary winding resistance. | [11 empty] | Lead + Other resisitance connected Sl: Rct; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 6; Lead + Other resisitance connected Isn: W
| Lead Resistance of the current loop from the CT to Relay | [11 empty] | Lead + Other resisitance connected Sl: Rl; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 1.097; Lead + Other resisitance connected Isn: W
| Burden of RED 670 Relay | [11 empty] | Lead + Other resisitance connected Sl: Sr; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 0.02; Lead + Other resisitance connected Isn: VA
For Close-in faults:
Ealreq = |  |  |  |  | 50000 |  | x | 1 |  | x | ( | 6 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
1000 | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
|  | = | 355.8511 |  | V
For Through faults (3-ph):
Ealreq = |  |  | 2 | x | 47858.0776 |  | x | 1 |  | x | ( | 6 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
1000 | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
|  | = | 681.214 |  | V
For Through faults (1-ph):
Ealreq = |  |  | 2 | x | 48245.339 |  | x | 1 |  | x | ( | 6 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
1000 | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
|  | = | 686.7263 |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer.
For Close-in faults:
Ealreq = |  |  | Ikmax |  | x | Isn |  | x | a | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
For Endzone-1 faults:
Ealreq = |  |  | Ikzone-1 |  | x | Isn |  | x | k | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipn; Sr: = | 1000 |  | A
| Max. primary fundamental frequency fault current for close-in faults | [6 empty] | +: Ikmax; Sr: = | 50000 |  | A
| Max. primary fundamental frequency fault current for zone-1 faults | [6 empty] | +: Ikzone-1; Sr: = | 48271.7306 |  | A | 3-phase
[17 empty] | 48587.1707 |  | A | 1-phase | bar: Sr
| CT secondary rated current . | [6 empty] | +: Isn; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | 6 |  | W
| Lead resistance between relay and CT sec. Terminals (2 way ) | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of RED 670 Relay | [15 empty] | 0.02 |  | VA | bar: + to Sr
High Speed Distance : Quadrilateral Characteristic
Factor for the Function of the primary time constant for the DC component in the fault current
[7 empty] | For the primary time constant tp | x: <= 400ms; x: :; (: a; +: =; Sr: 1
Factor for Function of the primary time constant for the DC component in the fault current
for a three phase fault at the set reach component in the fault current for of zone-1
[7 empty] | For the primary time constant tp | x: <= 200ms; x: :; (: k; +: =; Sr: 3
For Close-in faults:
[6 empty] | Since System tp |  |  |  | = | 127.2727 |  | ms, | a | = | 1
Ealreq = |  |  | 50000 |  | x | 1 |  | x | 1 | x | ( | 6 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
[6 empty] | 1000 | [10 empty] | x | 1 | bar: Sr
|  | = | 355.8511 |  | V
For Endzone-1 3-ph faults:
|  |  |  | Since 3-ph tp for this fault | [5 empty] | = | 111.098 |  | ms, | k | = | 3
Ealreq = |  |  | 48271.7306 |  | x | 1 |  | x | 3 | x | ( | 6 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | 1000 | [10 empty] | x | 1 | bar: Sr
|  | = | 1030.653 |  | V
For Endzone-1 1-ph faults:
|  |  |  | Since 1-ph tp for this fault | [5 empty] | = | 86.3428 |  | ms, | k | = | 3
Ealreq = |  |  | 48587.1707 |  | x | 1 |  | x | 3 | x | ( | 6 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | 1000 | [10 empty] | x | 1 | bar: Sr
|  | = | 1037.388 |  | V
Hence, highest Ealreq for Differential & Distance functions at | [7 empty] | Rct: 1000; Rl: A Tap =; Sr: 1037.388 |  | V
Therefore, the required knee point voltage of the CT.
(Vk in terms of Ealreq as per the Manufacturer )
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: 1037.388 |  | x | 0.8
[8 empty] | +: =; Sr: 829.9104 |  | V
|  |  | Available Vk |  |  | > | Required Vk | [14 empty] | >
|  |  |  | 2000 |  | > | 829.9104
[5 empty] | Hence CT is: |  | Suitably Dimensioned | [14 empty] | Suitably Dimensioned
| T1 |  | Core1 |  | 0 |  | (Diff. + Dist.) | [10 empty] | Connected devices: | RED670
| 0 | [17 empty] | 0
[7 empty] | Tap-1 | k: Tap-2; (: Tap-3 |  |  | 0
| CT Ratio: | [5 empty] | 1000 | k: 1500; (: -; +: /; Rl: 1; +: A
| Class of Accuracy: | [6 empty] | k: PX-A
| CT Resistance: | [6 empty] | x: Rct<; k: 8; (: W
| Knee Point Voltage: | [6 empty] | x: Vk>; k: 2000; (: V |  |  |  |  | Highest Vk required = |  | 708.7525
| Magnetizing Current: | [6 empty] | x: I0<; k: 40; (: mA at Vk
Other Burdens on same CT core:
| Burden of |  | RED670 |  |  |  | Sr' | x: =; k: 0.02; (: VA; +: Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | x: =; k: 0; (: VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1.097 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.097 |  | VA |  | =: =; Sl: 1.097; Isn: W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer.
For Close-in faults:
Ealreq = |  |  |  |  | Ikmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
For Through faults:
Ealreq = |  |  | 2 | x | Itmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: 1500; Isn: A
| Max. primary fundamental frequency fault current for close-in faults | [11 empty] | Sl: Ikmax; / (: =; Isn: 50000; Isn: A
| Max. primary fundamental frequency fault current for through fault | [13 empty] | Itmax | = | 47858.0776 |  | A | 3-phase
[16 empty] | = | 48245.339 |  | A | 1-phase
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: 8; Isn: W
| Lead Resistance of the current loop from the CT to Relay | [11 empty] | Sl: Rl; / (: =; Isn: 1.097; Isn: W
| Burden of RED 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
For Close-in faults:
Ealreq = |  |  |  |  | 50000 |  | x | 1 |  | x | ( | 8 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
1500 | bar: / ( to x
|  | = | 303.9007 |  | V
For Through faults (3-ph):
Ealreq = |  |  | 2 | x | 47858.0776 |  | x | 1 |  | x | ( | 8 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
1500 | bar: / ( to x
|  | = | 581.7642 |  | V
For Through faults (1-ph):
Ealreq = |  |  | 2 | x | 48245.339 |  | x | 1 |  | x | ( | 8 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
1500 | bar: / ( to x
|  | = | 586.4718 |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer. Ref Annexure-B
For Close-in faults:
Ealreq = |  |  | Ikmax |  | x | Isn |  | x | a | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
For Endzone-1 faults:
Ealreq = |  |  | Ikzone-1 |  | x | Isn |  | x | k | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipn; Sr: = | 1500 |  | A
| Max. primary fundamental frequency fault current for close-in faults | [6 empty] | +: Ikmax; Sr: = | 50000 |  | A
| Max. primary fundamental frequency fault current for zone-1 faults | [6 empty] | +: Ikzone-1; Sr: = | 48271.7306 |  | A | 3-phase
[17 empty] | 48587.1707 |  | A | 1-phase | bar: Sr
| CT secondary rated current . | [6 empty] | +: Isn; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | 8 |  | W
| Lead resistance between relay and CT sec. Terminals (2 way ) | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of RED 670 Relay | [15 empty] | 0.02 |  | VA | bar: + to Sr
High Speed Distance : Quadrilateral Characteristic
Factor for the Function of the primary time constant for the DC component in the fault current
[7 empty] | For the primary time constant tp | x: <= 400ms; x: :; (: a; +: =; Sr: 1
Factor for Function of the primary time constant for the DC component in the fault current
for a three phase fault at the set reach component in the fault current for of zone-1
[7 empty] | For the primary time constant tp | x: <= 200ms; x: :; (: k; +: =; Sr: 3
For Close-in faults:
[6 empty] | Since System tp |  |  |  | = | 127.2727 |  | ms, | a | = | 1
Ealreq = |  |  | 50000 |  | x | 1 |  | x | 1 | x | ( | 8 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
[6 empty] | 1500 | [10 empty] | x | 1 | bar: Sr
|  | = | 303.9007 |  | V
For Endzone-1 3-ph faults:
|  |  |  | Since 3-ph tp for this fault | [5 empty] | = | 111.098 |  | ms, | k | = | 3
Ealreq = |  |  | 48271.7306 |  | x | 1 |  | x | 3 | x | ( | 8 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | 1500 | [10 empty] | x | 1 | bar: Sr
|  | = | 880.1889 |  | V
For Endzone-1 1-ph faults:
|  |  |  | Since 1-ph tp for this fault | [5 empty] | = | 86.3428 |  | ms, | k | = | 3
Ealreq = |  |  | 48587.1707 |  | x | 1 |  | x | 3 | x | ( | 8 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | 1500 | [10 empty] | x | 1 | bar: Sr
|  | = | 885.9407 |  | V
Hence, highest Ealreq for Differential & Distance functions at | [7 empty] | Rct: 1500; Rl: A Tap =; Sr: 885.9407 |  | V
Therefore, the required knee point voltage of the CT.
(Vk in terms of Ealreq as per the Manufacturer )
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: 885.9407 |  | x | 0.8
[8 empty] | +: =; Sr: 708.7525 |  | V
|  |  | Available Vk |  |  | > | Required Vk
|  |  |  | 2000 |  | > | 708.7525
[5 empty] | Hence CT is: |  | Suitably Dimensioned
| T1 |  | Core1 |  | 0 |  | (Diff. + Dist.) | [10 empty] | Connected devices: | RED670
| 0 | [17 empty] | 0
[7 empty] | Tap-1 | k: Tap-2; (: Tap-3 |  |  | 0
| CT Ratio: | [5 empty] | 1000 | k: 1500; (: -; +: /; Rl: 1; +: A
| Class of Accuracy: | [6 empty] | (: PX-A
| CT Resistance: | [6 empty] | x: Rct<; (: -; +: W
| Knee Point Voltage: | [6 empty] | x: Vk>; (: -; +: V |  |  |  |  | Highest Vk required = |  | #VALUE!
| Magnetizing Current: | [6 empty] | x: I0<; (: -; +: mA at Vk
Other Burdens on same CT core:
| Burden of |  | RED670 |  |  |  | Sr' | x: =; k: 0.02; (: VA; +: Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | x: =; k: 0; (: VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.077 |  | VA |  | =: =; Sl: 1.077; Isn: W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer. Ref Annexure-B
For Close-in faults:
Ealreq = |  |  |  |  | Ikmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
For Through faults:
Ealreq = |  |  | 2 | x | Itmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: -; Isn: A
| Max. primary fundamental frequency fault current for close-in faults | [11 empty] | Sl: Ikmax; / (: =; Isn: 50000; Isn: A
| Max. primary fundamental frequency fault current for through fault | [13 empty] | Itmax | = | 47858.0776 |  | A | 3-phase
[16 empty] | = | 48245.339 |  | A | 1-phase
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: -; Isn: W
| Lead Resistance of the current loop from the CT to Relay | [11 empty] | Sl: Rl; / (: =; Isn: 1.097; Isn: W
| Burden of RED 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
For Close-in faults:
Ealreq = |  |  |  |  | 50000 |  | x | 1 |  | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
- | bar: / ( to x
|  | = | #VALUE! |  | V
For Through faults (3-ph):
Ealreq = |  |  | 2 | x | 47858.0776 |  | x | 1 |  | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
For Through faults (1-ph):
Ealreq = |  |  | 2 | x | 48245.339 |  | x | 1 |  | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer. Ref Annexure-B
For Close-in faults:
Ealreq = |  |  | Ikmax |  | x | Isn |  | x | a | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
For Endzone-1 faults:
Ealreq = |  |  | Ikzone-1 |  | x | Isn |  | x | k | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipn; Sr: = | - |  | A
| Max. primary fundamental frequency fault current for close-in faults | [6 empty] | +: Ikmax; Sr: = | 50000 |  | A
| Max. primary fundamental frequency fault current for zone-1 faults | [6 empty] | +: Ikzone-1; Sr: = | 48271.7306 |  | A | 3-phase
[17 empty] | 48587.1707 |  | A | 1-phase | bar: Sr
| CT secondary rated current . | [6 empty] | +: Isn; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | - |  | W
| Lead resistance between relay and CT sec. Terminals (2 way ) | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of RED 670 Relay | [15 empty] | 0.02 |  | VA | bar: + to Sr
High Speed Distance : Quadrilateral Characteristic
Factor for the Function of the primary time constant for the DC component in the fault current
[7 empty] | For the primary time constant tp | x: <= 400ms; x: :; (: a; +: =; Sr: 1
Factor for Function of the primary time constant for the DC component in the fault current
for a three phase fault at the set reach component in the fault current for of zone-1
[7 empty] | For the primary time constant tp | x: <= 200ms; x: :; (: k; +: =; Sr: 3
For Close-in faults:
[6 empty] | Since System tp |  |  |  | = | 127.2727 |  | ms, | a | = | 1
Ealreq = |  |  | 50000 |  | x | 1 |  | x | 1 | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
For Endzone-1 3-ph faults:
|  |  |  | Since 3-ph tp for this fault | [5 empty] | = | 111.098 |  | ms, | k | = | 3
Ealreq = |  |  | 48271.7306 |  | x | 1 |  | x | 3 | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
For Endzone-1 1-ph faults:
|  |  |  | Since 1-ph tp for this fault | [5 empty] | = | 86.3428 |  | ms, | k | = | 0
Ealreq = |  |  | 48587.1707 |  | x | 1 |  | x | 0 | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
Hence, highest Ealreq for Differential & Distance functions at | [7 empty] | Rct: -; Rl: A Tap =; Sr: #VALUE! |  | V
Therefore, the required knee point voltage of the CT.
(Summary of CT requirements for ABB relays, February 2008, formula no. 29, page 17/18)
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: #VALUE! |  | x | 0.8
[8 empty] | +: =; Sr: #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | Required Vk
|  |  |  | - |  | #VALUE! | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | x: Class; x: CT Resistance (W) @ 75OC; Rct: Limiting Secondary Voltage (Ual), V; Rl: Mag. Current (Io), mA at Vk; Sr: Relay / Instrument Type |  | CT Suitability
T1 | Core1 |  | 1000 |  | 1 | 120 | 6 | x: PX-A; x: 6; Rct: 2000; Rl: 30; Sr: RED670 |  | Suitably Dimensioned
|  |  | 1500 | [14 empty] | - | bar: x; Rct; Rl
|  |  | - | [14 empty] | - | bar: x; Rct; Rl

## BCU+OC-5P SEL751+7SJ85 (2)
7SJ85
| T1 |  | Core2 |  |  |  | (OC +BCU) | [10 empty] | Connected devices: | 7SJ85
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 700 |  | 300 |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | 5P | 20
| CT Resistance: |  |  |  |  | Rct< | 9 |  | W
| Rated Burden |  |  |  |  | PN | 8.5 |  | VA | [12 empty] | Under Dimensioned |  | 5
Other Burdens on same CT core:
| Burden of |  | 7SJ85 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of | [9 empty] | VA |  | PE | = | In | x | In | x | Rct
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1 | x | 1 | x | 9
| Total lead + other burden | [5 empty] | PL | = | 1.097 |  | VA |  |  | = | 9 |  | VA
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A | ** |  | This Current Must be Linked Later to Fault Setting
|  | CT Primary Current, | [13 empty] | Ipn | = | 700 |  | A
|  | Internal Burden, | [13 empty] | PE | = | 9 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.097 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN | = | 8.5 |  | VA
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 50000 |  | / | 700
[5 empty] | = | 71.4286
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 9 | + | 8.5 | ) / ( | 9 | + | 1.097 | )
[5 empty] | = | 34.6637
|  |  |  | Available Kssc' | = =: <; 71.4286 n: Required Kssc'
|  |  | 34.6637 |  | = =: <; 71.4286 n: 71.4286
|  |  |  | Hence CT is: | 71.4286 n: Under Dimensioned
** Assumed
| T1 |  | Core2 |  | 71.4286 x ( (: (OC +BCU) |  |  | Connected devices: | 7SJ85
| 0 | [17 empty] | 0
[5 empty] | 71.4286 x ( (: Tap-1; 71.4286 +: Tap-2; 71.4286 ) / (: Tap-3 |  |  |  | 0
| CT Ratio: |  |  |  | 71.4286 x ( (: 700; 71.4286 +: 300; 71.4286 ) / (: -; 71.4286 +: /; 71.4286 PL: 1; 71.4286 ): A |  |  |  | 0
| Class of Accuracy: |  |  |  | 71.4286 +: 5P; 71.4286 PN: 20
| CT Resistance: |  |  |  | 71.4286 PE: Rct<; 71.4286 +: 5; 71.4286 ) / (: W
| Rated Burden |  |  |  | 71.4286 PE: PN; 71.4286 +: 6; 71.4286 ) / (: VA | [6 empty] | Under Dimentioned |  |  | 5
Other Burdens on same CT core:
| Burden of |  | 7SJ85 |  | 71.4286 PE: =; 71.4286 +: 0.02; 71.4286 ) / (: VA; 71.4286 +: CT internal Burden
| Burden of |  | 0 |  | 71.4286 PE: =; 71.4286 +: 0; 71.4286 ) / (: VA
| Burden of |  | 0 |  | 71.4286 PE: =; 71.4286 +: 0; 71.4286 ) / (: VA
| Burden of |  | 0 |  | 71.4286 +: 0; 71.4286 ) / (: VA; 71.4286 +: PE; 71.4286 PL: =; 71.4286 ): In | x | In | x | Rct
| Total lead burden |  |  |  | 71.4286 PE: =; 71.4286 +: 1.077; 71.4286 ) / (: VA; 71.4286 PL: =; 71.4286 ): 1 | x | 1 | x | 5
| Total lead + other burden |  |  |  | 71.4286 x ( (: PL; 71.4286 PE: =; 71.4286 +: 1.097; 71.4286 ) / (: VA; 71.4286 PL: =; 71.4286 ): 5 |  | VA
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 300 |  | A
|  | Internal Burden, | [13 empty] | PE | = | 5 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.097 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN | = | 6 |  | VA
|  |  |  | Required Kssc' | = =: =; 71.4286 n: Itkmax; 71.4286 PE: /; 71.4286 +: Ipn
[5 empty] | = | 50000 |  | / | 300
[5 empty] | = | 166.6667
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 5 | + | 6 | ) / ( | 5 | + | 1.097 | )
[5 empty] | = | 36.0832
|  |  |  | Available Kssc' | = =: <; 166.6667 n: Required Kssc'
|  |  | 36.0832 |  | = =: <; 166.6667 n: 166.6667
|  |  |  | Hence CT is: | 166.6667 n: Under Dimentioned
| T1 |  | Core2 |  | 166.6667 x ( (: (OC +BCU) |  |  | Connected devices: | 7SJ85
| 0 | [17 empty] | 0
[5 empty] | 166.6667 x ( (: Tap-1; 166.6667 +: Tap-2; 166.6667 ) / (: Tap-3 |  |  |  | 0
| CT Ratio: |  |  |  | 166.6667 x ( (: 700; 166.6667 +: 300; 166.6667 ) / (: -; 166.6667 +: /; 166.6667 PL: 1; 166.6667 ): A
| Class of Accuracy: |  |  |  | 166.6667 ) / (: 5P; 166.6667 PE: 20
| CT Resistance: |  |  |  | 166.6667 PN: Rct<; 166.6667 ) / (: -; 166.6667 +: W
| Rated Burden |  |  |  | 166.6667 PN: PN; 166.6667 ) / (: -; 166.6667 +: VA | [6 empty] | #VALUE!
Other Burdens on same CT core:
| Burden of |  | 7SJ85 |  | 166.6667 PE: =; 166.6667 +: 0.02; 166.6667 ) / (: VA; 166.6667 +: CT internal Burden
| Burden of |  | 0 |  | 166.6667 PE: =; 166.6667 +: 0; 166.6667 ) / (: VA
| Burden of |  | 0 |  | 166.6667 PE: =; 166.6667 +: 0; 166.6667 ) / (: VA; 166.6667 +: PE; 166.6667 PL: =; 166.6667 ): In | x | In | x | Rct
| Total lead burden |  |  |  | 166.6667 PE: =; 166.6667 +: 1.077; 166.6667 ) / (: VA; 166.6667 PL: =; 166.6667 ): 1 | x | 1 | x | -
| Total lead + other burden |  |  |  | 166.6667 x ( (: PL; 166.6667 PE: =; 166.6667 +: 1.097; 166.6667 ) / (: VA; 166.6667 PL: =; 166.6667 ): #VALUE! |  | VA
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 300 |  | A
|  | Internal Burden, | [13 empty] | PE | = | #VALUE! |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.097 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN | = | - |  | VA
|  |  |  | Required Kssc' | = =: =; 166.6667 n: Itkmax; 166.6667 PE: /; 166.6667 +: Ipn
[5 empty] | = | 50000 |  | / | 300
[5 empty] | = | 166.6667
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 1.097 | )
[5 empty] | = | #VALUE!
|  |  |  | Available Kssc' | = =: #VALUE!; 166.6667 n: Required Kssc'
|  |  | #VALUE! |  | = =: #VALUE!; 166.6667 n: 166.6667
|  |  |  | Hence CT is: | 166.6667 n: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | 166.6667 n: CT Cable m/mm2; 166.6667 PE: Class; 166.6667 PN: CT Resistance (W) @ 75OC; 166.6667 PE: Rated Burden of CT, VA | Relay / Instrument Type |  | CT Suitability
T1 | Core2 |  | 700 |  | 1 | 120 | 6 | 5P | 20 | 9 |  | 8.5 |  | - |  | 7SJ85 |  | Under Dimensioned
|  |  | 300 |  | 166.6667 PN: 5; 166.6667 PE: 6; 166.6667 PL: - |  |  | Under Dimentioned
|  |  | - | [14 empty] | - | bar: 166.6667 PN; 166.6667 PE; 166.6667 PL

## Tariff Check-0.2FS (3) (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | 33kV DIAMOND CABLE FEEDERS | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core4 |  |  | (Tariff Meter- Check) | [10 empty] | Connected devices: | XC-RACK
GOSSEN
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 600 |  | 200 |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.2FS10
| CT Resistance: |  |  |  | Rct< | 8 |  | W
| Factor of Safety |  |  |  | FS | 10 | [13 empty] | Suitable Dimensions
| Rated Burden |  |  |  | PN | 7.5 |  | VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [8 empty] | rec670 | 100A for 1 S
| Burden of |  | GOSSEN |  |  |  | = | 0.25 |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 8
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 8 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 1.335 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 600 |  | A
| Internal Burden, | [10 empty] | PE | = | 8 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 1.335 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | n | = | 10
| Safety Factor among all connected devices Fs (min) | [11 empty] | = | 20 |  | ** | Assumed
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 1.335
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 10 | x ( ( | 8 | + | 7.5 | ) / ( | 8 | + | 1.335 | )
[7 empty] | = | 16.6041
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.335 FS: Total Connected Burden; 1.335 ): …cond.1
[5 empty] | 7.5 |  | = =: >; 1.335 FS: 1.335; 1.335 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.335 FS: Effective Safety Factor of CT, FS'; 1.335 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.335 FS: 16.6041; 1.335 ): Satisfied
[6 empty] | Hence CT is: | 1.335 FS: Suitable Dimensions
| T1 |  | Core4 |  |  | (Tariff Meter- Check) | 1.335 ): Connected devices: | XC-RACK
| 0 | [16 empty] | GOSSEN
[6 empty] | Tap-1 | 1.335 FS: Tap-2; 1.335 PE: Tap-3
| CT Ratio: |  |  |  |  | 600 | 1.335 FS: 200; 1.335 PE: -; 1.335 PN: /; 1.335 ) / (: 1; 1.335 PE: A
| Class of Accuracy: | [5 empty] | 1.335 FS: 0.2FS10
| CT Resistance: | [5 empty] | = =: Rct<; 1.335 FS: 4; 1.335 PE: W
| Factor of Safety | [5 empty] | = =: FS; 1.335 FS: 10 |  |  | Suitable Dimensions
| Rated Burden | [5 empty] | = =: PN; 1.335 FS: 5; 1.335 PE: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 1.335 FS: 0.008; 1.335 PE: VA; 1.335 PN: CT internal Burden
| Burden of |  | GOSSEN |  |  |  | = =: =; 1.335 FS: 0.25; 1.335 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 4
| Total lead burden | [5 empty] | = =: =; 1.335 FS: 1.077; 1.335 PE: VA; 1.335 ) / (: =; 1.335 PE: 4; 1.335 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.335 FS: 1.335; 1.335 PE: VA
| CT Primary Current, | [5 empty] | 1.335 PN: Ipn; 1.335 ) / (: =; 1.335 PE: 200; 1.335 PL: A
| Internal Burden, | [5 empty] | 1.335 PN: PE; 1.335 ) / (: =; 1.335 PE: 4; 1.335 PL: VA
| Burden of CT Leads and burden of connected devices | [5 empty] | 1.335 PN: PL; 1.335 ) / (: =; 1.335 PE: 1.335; 1.335 PL: VA
| Rated Secondary Current, | [5 empty] | 1.335 PN: In; 1.335 ) / (: =; 1.335 PE: 1; 1.335 PL: A
| CT Safety Factor | [5 empty] | 1.335 PN: n; 1.335 ) / (: =; 1.335 PE: 10
| Safety Factor among all connected devices Fs (min) | [5 empty] | 1.335 ) / (: =; 1.335 PE: 20; 1.335 PL: **; 1.335 ): Assumed
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.335 +: Fs(min); 1.335 PL: =; 1.335 ): 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.335 FS: Connected devices burden; 1.335 PE: +; 1.335 +: Lead Burden
[7 empty] | = | 1.335
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 10 | x ( ( | 4 | + | 5 | ) / ( | 4 | + | 1.335 | )
[7 empty] | = | 16.8697
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.335 FS: Total Connected Burden; 1.335 ): …cond.1
[5 empty] | 5 |  | = =: >; 1.335 FS: 1.335; 1.335 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.335 FS: Effective Safety Factor of CT, FS'; 1.335 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.335 FS: 16.8697; 1.335 ): Satisfied
[6 empty] | Hence CT is: | 1.335 FS: Suitable Dimensions
| T1 |  | Core4 |  |  | (Tariff Meter- Check)
0
[6 empty] | Tap-1 | 1.335 FS: Tap-2; 1.335 PE: Tap-3
| CT Ratio: |  |  |  |  | 600 | 1.335 FS: 200; 1.335 PE: -; 1.335 PN: /; 1.335 ) / (: 1; 1.335 PE: A
| Class of Accuracy: | [5 empty] | 1.335 PE: 0.2FS10
| CT Resistance: | [5 empty] | 1.335 x ( (: Rct<; 1.335 PE: -; 1.335 PN: W
| Factor of Safety | [18 empty] | #VALUE! | bar: 1.335 x ( ( to 1.335 +
| Rated Burden | [5 empty] | 1.335 x ( (: PN; 1.335 PE: -; 1.335 PN: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 1.335 FS: 0.008; 1.335 PE: VA; 1.335 PN: CT internal Burden
| Burden of |  | GOSSEN |  |  |  | = =: =; 1.335 FS: 0.25; 1.335 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [5 empty] | = =: =; 1.335 FS: 1.077; 1.335 PE: VA; 1.335 ) / (: =; 1.335 PE: #VALUE!; 1.335 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.335 FS: 1.335; 1.335 PE: VA
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.335 +: Fs(min); 1.335 PL: =; 1.335 ): 20
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.335 FS: CT Int. Burden; 1.335 +: +; 1.335 PN: Connected Burden
[7 empty] | = | #VALUE! |  | + | 1.335
[7 empty] | = | #VALUE!
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | - | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 1.335 | )
[7 empty] | = | #VALUE!
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; #VALUE! FS: Total Connected Burden; #VALUE! ): …cond.1
[5 empty] | - |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; #VALUE! FS: Effective Safety Factor of CT, FS'; #VALUE! ): …cond.2
[5 empty] | 20 |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
[6 empty] | Hence CT is: | #VALUE! FS: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; #VALUE! x ( (: CT Resistance (W) @ 75OC; #VALUE! +: Rated Burden VA; #VALUE! +: Relay / Instrument Type; #VALUE! ): CT Suitability
T1 | Core4 |  | 600 | 1 | 120 | 6 | = =: 0.2FS10; #VALUE! x ( (: 8; #VALUE! +: 7.5; #VALUE! ) / (: -; #VALUE! +: XC-RACK GOSSEN; #VALUE! ): Suitable Dimensions
|  |  | 200 |  |  |  | #VALUE! x ( (: 4; #VALUE! +: 5; #VALUE! ) / (: -; #VALUE! ): Suitable Dimensions
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )

## BAY2 (hidden)
Transformer (BC2 - 11, 07,06)
Back to
INDEX

## HVC1 - REF650 (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AK | Checked By |  |  | LN | Transformer | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core1 | [14 empty] | Connected devices: | REF650
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 1250 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [12 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Total lead burden | [6 empty] | = | 2.7035 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead + other burden | [5 empty] | PL | = | 2.7235 |  | VA |  |  | = | 5 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 1250 |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 750 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 5 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 2.7235 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN | = | 43.75
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | 750 |  | x | 1 | ) / | 20 | ) - | 5
|  |  | = | 43.75 |  | VA
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 50000 |  | / | 1250
[5 empty] | = | 40
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 5 | + | 43.75 | ) / ( | 5 | + | 2.7235 | )
[5 empty] | = | 126.2381
|  |  |  | Available Kssc' | = =: >; 40 n: Required Kssc'
|  |  | 126.2381 |  | = =: >; 40 n: 40
|  |  |  | Hence CT is: | 40 n: Suitably Dimentioned
| T1 |  | Core1 |  | 40 x ( (: 0 |  |  | Connected devices: | REF650
| 0 | [17 empty] | 0
[5 empty] | 40 x ( (: Tap-1; 40 +: Tap-2; 40 ) / (: Tap-3 |  |  |  | 0
| CT Ratio: |  |  |  | 40 x ( (: 1250; 40 +: -; 40 ) / (: -; 40 +: /; 40 PL: 1; 40 ): A
| Class of Accuracy: |  |  |  | 40 +: PX-B
| CT Resistance: |  |  |  | 40 PE: Rct<; 40 +: 5; 40 ) / (: W
| Knee Point Voltage: |  |  |  | 40 PE: Vk>; 40 +: 500; 40 ) / (: V | [6 empty] | #VALUE!
| Magnetizing Current: |  |  |  | 40 PE: I0<; 40 +: 50; 40 ) / (: mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  | 40 PE: =; 40 +: 0.02; 40 ) / (: VA; 40 +: CT internal Burden
| Burden of |  | 0 |  | 40 PE: =; 40 +: 0; 40 ) / (: VA
| Burden of |  | 0 |  | 40 PE: =; 40 +: 0; 40 ) / (: VA; 40 +: PE; 40 PL: =; 40 ): In | x | In | x | Rct
| Total lead burden |  |  |  | 40 PE: =; 40 +: 2.7035; 40 ) / (: VA; 40 PL: =; 40 ): 1 | x | 1 | x | 5
| Total lead + other burden |  |  |  | 40 x ( (: PL; 40 PE: =; 40 +: 2.7235; 40 ) / (: VA; 40 PL: =; 40 ): 5 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 40000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 500 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 5 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 2.7235 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | 500 |  | x | 1 | ) / | 20 | ) - | 5
|  |  | = | 27.5 | bar: 40 n
ABB
|  |  |  | Required Kssc' | = =: =; 40 n: Itkmax; 40 PE: /; 40 +: Ipn
[5 empty] | = | 40000 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 5 | + | 27.5 | ) / ( | 5 | + | 2.7235 | )
[5 empty] | = | 84.1587
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | 84.1587 |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
ABB
| T1 |  | Core1 |  | #VALUE! x ( (: 0 |  |  | Connected devices: | REF650
| 0 | [17 empty] | 0
[5 empty] | #VALUE! x ( (: Tap-1; #VALUE! +: Tap-2; #VALUE! ) / (: Tap-3 |  |  |  | 0
| CT Ratio: |  |  |  | #VALUE! x ( (: 1250; #VALUE! +: -; #VALUE! ) / (: -; #VALUE! +: /; #VALUE! PL: 1; #VALUE! ): A
| Class of Accuracy: |  |  |  | #VALUE! ) / (: PX-B
| CT Resistance: |  |  |  | #VALUE! PN: Rct<; #VALUE! ) / (: 3; #VALUE! +: W
| Knee Point Voltage: |  |  |  | #VALUE! PN: Vk>; #VALUE! ) / (: 300; #VALUE! +: V | [6 empty] | #VALUE!
| Magnetizing Current: |  |  |  | #VALUE! PN: I0<; #VALUE! ) / (: 75; #VALUE! +: mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA; #VALUE! +: CT internal Burden
| Burden of |  | 0 |  | #VALUE! PE: =; #VALUE! +: 0; #VALUE! ) / (: VA
| Burden of |  | 0 |  | #VALUE! PE: =; #VALUE! +: 0; #VALUE! ) / (: VA; #VALUE! +: PE; #VALUE! PL: =; #VALUE! ): In | x | In | x | Rct
| Total lead burden |  |  |  | #VALUE! PE: =; #VALUE! +: 2.7035; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): 1 | x | 1 | x | 3
| Total lead + other burden |  |  |  | #VALUE! x ( (: PL; #VALUE! PE: =; #VALUE! +: 2.7235; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): 3 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 40000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 300 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 3 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 2.7235 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | 300 |  | x | 1 | ) / | 20 | ) - | 3
|  |  | = | 16.5 | bar: #VALUE! n
ABB
|  |  |  | Required Kssc' | = =: =; #VALUE! n: Itkmax; #VALUE! PE: /; #VALUE! +: Ipn
[5 empty] | = | 40000 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 3 | + | 16.5 | ) / ( | 3 | + | 2.7235 | )
[5 empty] | = | 68.1401
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | 68.1401 |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
ABB
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  | #VALUE! n: CT Cable m/mm2; #VALUE! PE: Class; #VALUE! PN: Rct @ 75OC (Ω); #VALUE! PE: Rated Vk (V); #VALUE! PL: Im @ Vk (mA) | Connected Devices |  | CT Suitability
T1 | Core1 |  | 1250 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 |  | REF650 |  | Suitably Dimentioned
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL

## MFAC+MVTP (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | Transformer | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core2 | [14 empty] | Connected devices: | MFAC
MVTP
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 1250 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [11 empty] | #REF!
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | MFAC |  |  |  |  | = | 0.02 |  | VA
| Burden of |  | MVTP |  |  |  |  | = | 0.02 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.117 |  | VA
|  | Max primary through fault current for which stability is required | [13 empty] | IF | = | 47858.0776 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 1250 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | 38.2865 |  | A
|  | Resistance of each lead between the relay and CT | [13 empty] | 2Rw | = | 1.117 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 25000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | 20 |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 2 | x | IF |  | x ( | Rct |  | + | 2Rw |  | )
|  |  | = | 2 | x | 38.2865 |  | x ( | 5 |  | + | 1.117 |  | )
|  |  | = | 468.3983
Adequacy Check
[5 empty] | Available Vk | > | Required Vk
|  |  |  | 750 |  | > | 468.3983
[5 empty] | Hence CT is: |  | Suitably Dimentioned
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) |  | Connected Devices |  | CT Suitability
T1 | Core2 |  | 1250 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 |  | MFAC MVTP |  | Suitably Dimentioned
|  |  | - | [6 empty] | - |  | - |  | - |  |  |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  |  |  | -

## BUP BCU(2) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AK | Checked By |  |  | LN | Transformer | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core3 | [14 empty] | Connected devices: | REF650
REC670
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | IDM+18
| CT Ratio: | [5 empty] | 1250 |  | - |  | - |  | / | 1 | A |  |  |  | P141
| Class of Accuracy: | [5 empty] | 5P20 | [11 empty] | PQ100
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W | [9 empty] | PM7500
| Knee Point Voltage: |  |  |  |  | Vk> |  |  | V | [11 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA
| Burden of |  | IDM+18 |  |  |  |  | = | 0.058 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | P141 | [5 empty] | 0.04
| Burden of |  | PQ100
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead + other burden | [5 empty] | PL | = | 1.215 |  | VA |  |  | = | 5 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula: | [20 empty] | The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 1250 |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 0 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 5 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.215 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN | = | 30
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | 0 |  | x | 1 | ) / | 20 | ) - | 5
|  |  | = | -5 |  | VA
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 50000 |  | / | 1250
[5 empty] | = | 40
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 5 | + | 30 | ) / ( | 5 | + | 1.215 | )
[5 empty] | = | 112.6303
|  |  |  | Available Kssc' | = =: >; 40 n: Required Kssc'
|  |  | 112.6303 |  | = =: >; 40 n: 40
|  |  |  | Hence CT is: | 40 n: Suitably Dimentioned
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  | 40 n: CT Cable m/mm2; 40 PE: Class; 40 PN: CT Resistance (W) @ 75OC; 40 PE: Limiting Secondary Voltage (Ual), V; 40 PL: Mag. Current (Io), mA at Vk | Relay / Instrument Type |  | CT Suitability
T1 | Core3 |  | 1250 |  | 1 | 120 | 6 | 5P20 | #REF! | 5 |  | - |  | - |  | REF650 REC670 IDM+18 |  | Suitably Dimentioned
|  |  | - | [14 empty] | - | bar: 40 PN; 40 PE; 40 PL
|  |  | - | [14 empty] | - | bar: 40 PN; 40 PE; 40 PL

## BBP FU1 - REB500 (2) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | Transformer | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core4 | [14 empty] | Connected devices: | REB500
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [12 empty] | #REF!
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 5 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.087 |  | VA
CT-Requirements for BB Protection
|  | Maximum Primary Fault Current | [13 empty] | Isc | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2500 |  | A
|  | Rated Voltage | [13 empty] | UN2 | = | 400 |  | kV
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 750 |  | V
|  | Internal Resistance CT | [13 empty] | Rct | = | 5 |  | VA
|  | Conn. Lead + Relay Burden | [13 empty] | RL | = | 1.087 |  | VA
|  | Rated Secondary Current, | [13 empty] | Isc | = | 1 |  | A
|  | Nominal Frequency of the network | [13 empty] | fn | = | 50
Required OC factor condition. 1:
At Max. Through fault current CT’s shall not saturate for currents below 5 times rated current.
[8 empty] | n' | = | Isc
5 * Ipn
Required OC factor Condition 2:
n2' >= 10 for TN <=120 msec
n2' >= 20 for 120ms <= TN <=300 ms
| Where, |  | n' = Required OC factor
Isc = max. bus fault current
Ipn = Rated primary current (A)
[23 empty] | ** | Rated Bus fault current
Required OC factor condition 1:
|  | n'(1) | = | 50000
5 x 2500
|  | n'(1) | = | 4
Required OC factor condition 2:
|  |  |  | TN = | 1 |  | X | X
[6 empty] | 2* ϖ* fn |  | R
[5 empty] | 1 |  |  |  | x | 15
|  |  | TN | = | 2 * 3.14 * 50
|  |  |  | = | 0.047771 |  | sec
|  |  | TN | = | 47.7707 |  | ms
| Hence n'(2) 10 |  |  | = | 10
Required OC factor n' >= max( n'(1) ; n'(2))
n' >=max(4 ; 10)
Therefore
|  | n' | = | 10 |  | Necessary Condition
Required secondary equivalent limiting secondary e.m.f
Eal >= n' *(RCT+RL+Rr)*Isn
| = | 10 | x | ( | 5 |  | + | 1.087 | + | 0.01 | ) | x | 1
| Eal | = | 60.9702 | V
| According to IEC 61869 class PX | [7 empty] | Eknee |  | > |  | 0.8*Eal
[11 empty] | = |  | 48.7762
[5 empty] | With design margin 120% | [5 empty] | = |  | 58.5314
[10 empty] | Available Vk | > | Required Vk
[8 empty] | 750 |  |  | > | 58.5314
[10 empty] | Hence CT is: |  | Suitable Dimensions
| T1 |  | Core4 |  |  |  | 0 | [10 empty] | Connected devices: | REB500
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [7 empty] | PX-B
| CT Resistance: | [6 empty] | Rct< | 9.3 |  | W
| Knee Point Voltage: | [6 empty] | Vk> | 500 |  | V | [10 empty] | Required Vk
| Magnetizing Current: | [6 empty] | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 9.3
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 9.3 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.087 |  | VA
CT-Requirements for BB Protection
|  | Maximum Primary Fault Current | [13 empty] | Isc | = | 31500 |  | A | **
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Voltage | [13 empty] | UN2 | = | 33 |  | kV
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 500 |  | V
|  | Internal Resistance CT | [13 empty] | Rct | = | 9.3 |  | VA
|  | Conn. Lead + Relay Burden | [13 empty] | RL | = | 1.087 |  | VA
|  | Rated Secondary Current, | [13 empty] | Isc | = | 1 |  | A
|  | Nominal Frequency of the network | [13 empty] | fn | = | 50
Required OC factor condition. 1:
At Max. Through fault current CT’s shall not saturate for currents below 5 times rated current.
[8 empty] | n' | = | Isc
5 * Ipn
Required OC factor Condition 2:
n2' >= 10 for TN <=120 msec
n2' >= 20 for 120ms <= TN <=300 ms
Where,
n' = Required OC factor
Isc = max. bus fault current
Ipn = Rated primary current (A)
[10 empty] | ** | Rated Bus fault current
Required OC factor condition 1:
|  | n'(1) | = | 31500
5 x -
|  | n'(1) | = | #VALUE!
Required OC factor condition 2:
|  |  |  | TN = | 1 |  | X | X
[6 empty] | 2* ϖ* fn |  | R
| As per Transco Standard for 33kV system X/R | [11 empty] | = | #REF!
[5 empty] | 1 |  |  |  | x | #REF!
|  |  | TN | = | 2 * 3.14 * 50
|  |  |  | = | #REF! |  | sec
|  |  | TN | = | #REF! |  | ms
| Hence n'(2) 10 |  |  | = | 10
Required OC factor n' >= max( n'(1) ; n'(2))
n' >=max(3.15 ; 10)
Therefore
|  | n' | = | #VALUE! |  | Necessary Condition
Required secondary equivalent limiting secondary e.m.f
Eal >= n' *(RCT+RL+Rr)*Isn
| = | #VALUE! | x | ( | 9.3 |  | + | 1.087 | + | 0.01 | ) | x | 1
| Eal | = | #VALUE! | V
| According to IEC 61869 class PX | [7 empty] | Eknee |  | > |  | 0.8*Eal
[11 empty] | = |  | #VALUE!
[5 empty] | With design margin 120% | [5 empty] | = |  | #VALUE!
[10 empty] | Available Vk | #VALUE! | Required Vk
[9 empty] | 500 |  | #VALUE! | #VALUE!
[10 empty] | Hence CT is: |  | #VALUE!
| T1 |  | Core4 |  |  |  | 0 | [10 empty] | Connected devices: | REB500
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [9 empty] | PX-B
| CT Resistance: | [8 empty] | Rct< | - |  | W
| Knee Point Voltage: | [8 empty] | Vk> | - |  | V | [8 empty] | #VALUE!
| Magnetizing Current: | [8 empty] | I0< | - |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | #VALUE! |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.087 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 1 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | - |  | V
|  | Internal Burden, | [13 empty] | PE | = | #VALUE! |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.087 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | - |  | x | 1 | ) / | 20 | ) - | #VALUE!
|  |  | = | #VALUE! |  | VA
The CT requirement is as follows:
where
| n' | ³ | n1 |  | --- (i) |  |  |  |  | n' | = | The effective accuracy limiting factor
| n' | ³ | n2 |  | --- (ii) | [5 empty] | = | n x (PN + PE) / (PL + PE)
[10 empty] | n1 | = | Itkmax / (5 x Ipn)
[10 empty] | n2 | = | 10 |  | ...for | TP | £ | 120 | msec
[11 empty] | = | 20 |  | ...for | TP | £ | 300 | msec
Calculation for n1: | [9 empty] | n1 | = | Itmax |  | / ( | 5 | x | Ipn |  | )
[11 empty] | = | 1 |  | / ( | 5 | x | - |  | )
[11 empty] | = | #VALUE!
Calculation for n2: |  |  |  | Since Tp |  | = | #REF! |  | , | n2 | = | #REF!
Calculation for n': | [5 empty] | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[6 empty] | = | 20 | x ( ( | #VALUE! | + | #VALUE! | ) / ( | #VALUE! | + | 1.087 | )
[6 empty] | = | #VALUE!
Checking the conditions ---(i) and ---(ii) mentioned aove:
|  |  | #VALUE! |  | #VALUE! | =: #VALUE!; PE: --- (i)
|  |  | #VALUE! |  | #VALUE! | =: #REF!; PE: --- (ii)
|  |  |  | Hence CT is: |  | =: #VALUE!
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | =: CT Cable m/mm2; x ( (: Class; +: CT Resistance (W) @ 75OC; ) / (: Limiting Secondary Voltage (Ual), V; +: Mag. Current (Io), mA at Vk; ): Relay / Instrument Type |  | CT Suitability
T1 | Core4 |  | 2500 |  | 1 | 120 | 6 | PX-B | #REF! | 5 |  | 750 |  | 60 |  | REB500 |  | Suitable Dimensions
|  |  | - | [14 empty] | - | bar: +; ) / (; +
|  |  | - | [14 empty] | - | bar: +; ) / (; +

## BBP 743(2) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | Transformer | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core5 | [14 empty] | Connected devices: | P743
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [12 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.177 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 50000 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 2500 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | 20 |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 1.177 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 50000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | 20 |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | 20 |  | x ( | 5 |  | + | 1.177 |  | )
|  |  | = | 61.7702
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 20 |  | x ( | 5 |  | + | 1.177 |  | )
|  |  | = | 123.5404
Adequacy Check
Criteria I
[5 empty] | Available Vk | > | Required Vk |  |  |  | (Criteria I)
|  |  |  | 750 |  | > | 61.7702
[5 empty] | Hence: |  | Criteria I |  | is | Satisfied
Criteria II
[5 empty] | Available Vk | > | Required Vk |  |  |  | (Criteria II)
|  |  |  | 750 |  | > | 123.5404
[5 empty] | Hence: |  | Criteria II |  | is | Satisfied
[5 empty] | Hence CT is: |  | Suitably Dimentioned
| T1 |  | Core5 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | P743
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [7 empty] | PX-B
| CT Resistance: | [6 empty] | Rct< |  |  | W
| Knee Point Voltage: | [6 empty] | Vk> |  |  | V | [10 empty] | Under Dimentioned
| Magnetizing Current: | [6 empty] | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.177 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 50000 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 2500 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | 20 |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 1.177 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 50000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | 20 |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | 20 |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | 11.7702
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 20 |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | 23.5404
Adequacy Check
Criteria I
[5 empty] | Available Vk | < | Required Vk |  |  |  | (Criteria I)
|  |  |  | 0 |  | < | 11.7702
[5 empty] | Hence: |  | Criteria I |  | is | Not Satisfied
Criteria II
[5 empty] | Available Vk | < | Required Vk |  |  |  | (Criteria II)
|  |  |  | 0 |  | < | 23.5404
[5 empty] | Hence: |  | Criteria II |  | is | Not Satisfied
[5 empty] | Hence CT is: |  | Under Dimentioned
ABB
| T1 |  | Core5 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | P743
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [9 empty] | PX-B
| CT Resistance: | [8 empty] | Rct< |  |  | W
| Knee Point Voltage: | [8 empty] | Vk> |  |  | V | [8 empty] | #VALUE!
| Magnetizing Current: | [8 empty] | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.177 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 50000 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | - |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | #VALUE! |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 1.177 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 50000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | #VALUE! |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | #VALUE! |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | #VALUE!
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | #VALUE! |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | #VALUE!
ABB
Adequacy Check
Criteria I
[5 empty] | Available Vk | #VALUE! | Required Vk |  |  |  | (Criteria I)
|  |  |  | 0 |  | #VALUE! | #VALUE!
[5 empty] | Hence: |  | Criteria I |  | is | #VALUE!
Criteria II
[5 empty] | Available Vk | #VALUE! | Required Vk |  |  |  | (Criteria II)
|  |  |  | 0 |  | #VALUE! | #VALUE!
[5 empty] | Hence: |  | Criteria II |  | is | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
ABB
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | CT Resistance (W) @ 75OC |  | Limiting Secondary Voltage (Ual), V |  | Mag. Current (Io), mA at Vk |  | Relay / Instrument Type |  | CT Suitability
T1 | Core5 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 |  | P743 |  | Suitably Dimentioned
|  |  | - | [6 empty] | - |  | - |  | - |  |  |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  |  |  | -

## BAY3 (hidden)
Line Protection 400kV FEEDERS ( BC3 - 09, 05, 03 ,02, 04, 08)
Back to
INDEX

## RED670_2.2C42-X (2) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV CABLE FEEDERS | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core1 |  |  |  | (Diff. + Dist.) | [10 empty] | Connected devices: | RED670 |  | Note: CT requirements for other protection functions are different. Pl. refer to Application Manual
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 600 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX
| CT Resistance: |  |  |  |  | Rct < | 4 |  | W
| Knee Point Voltage: |  |  |  |  | Vk > | 800 |  | V | [11 empty] | Highest Vk required = |  | 994.4866
| Magnetizing Current: |  |  |  |  | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | RED670 |  |  |  | Sr' | = | 0.02 |  | VA |  | Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Burden of | [6 empty] | = |  |  | VA |  |  | = | 1.097 | / ( | 1 | x | 1 | )
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  | Lead + Other resisitance connected =: =; Lead + Other resisitance connected Sl: 1.097; Lead + Other resisitance connected Isn: W
| Total lead + other burden | [5 empty] | Sl | = | 1.097 |  | VA
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer.
For Close-in faults:
Ealreq = |  |  |  |  | Ikmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
For Through faults:
Ealreq = |  |  | 2 | x | Itmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
| Equivalent Secondary emf. Required | [11 empty] | Lead + Other resisitance connected Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Lead + Other resisitance connected Sl: Ipn; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 600; Lead + Other resisitance connected Isn: A
| Max. primary fundamental frequency fault current for close-in faults | [11 empty] | Lead + Other resisitance connected Sl: Ikmax; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 50000; Lead + Other resisitance connected Isn: A
| Max. primary fundamental frequency fault current for through fault | [13 empty] | Itmax | = | 47858.0776 |  | A | 3-phase
[16 empty] | = | 48245.339 |  | A | 1-phase
| CT secondary rated current | [11 empty] | Lead + Other resisitance connected Sl: Isn; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 1; Lead + Other resisitance connected Isn: A
| Relay rated current | [11 empty] | Lead + Other resisitance connected Sl: Ir; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 1; Lead + Other resisitance connected Isn: A
| CT secondary winding resistance. | [11 empty] | Lead + Other resisitance connected Sl: Rct; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 4; Lead + Other resisitance connected Isn: W
| Lead Resistance of the current loop from the CT to Relay | [11 empty] | Lead + Other resisitance connected Sl: Rl; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 1.097; Lead + Other resisitance connected Isn: W
| Burden of RED 670 Relay | [11 empty] | Lead + Other resisitance connected Sl: Sr; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 0.02; Lead + Other resisitance connected Isn: VA
For Close-in faults:
Ealreq = |  |  |  |  | 50000 |  | x | 1 |  | x | ( | 4 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
600 | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
|  | = | 426.4185 |  | V
For Through faults (3-ph):
Ealreq = |  |  | 2 | x | 47858.0776 |  | x | 1 |  | x | ( | 4 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
600 | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
|  | = | 816.3029 |  | V
For Through faults (1-ph):
Ealreq = |  |  | 2 | x | 48245.339 |  | x | 1 |  | x | ( | 4 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
600 | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
|  | = | 822.9083 |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer.
For Close-in faults:
Ealreq = |  |  | Ikmax |  | x | Isn |  | x | a | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
For Endzone-1 faults:
Ealreq = |  |  | Ikzone-1 |  | x | Isn |  | x | k | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipn; Sr: = | 600 |  | A
| Max. primary fundamental frequency fault current for close-in faults | [6 empty] | +: Ikmax; Sr: = | 50000 |  | A
| Max. primary fundamental frequency fault current for zone-1 faults | [6 empty] | +: Ikzone-1; Sr: = | 48271.7306 |  | A | 3-phase
[17 empty] | 48587.1707 |  | A | 1-phase | bar: Sr
| CT secondary rated current . | [6 empty] | +: Isn; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | 4 |  | W
| Lead resistance between relay and CT sec. Terminals (2 way ) | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of RED 670 Relay | [15 empty] | 0.02 |  | VA | bar: + to Sr
High Speed Distance : Quadrilateral Characteristic
Factor for the Function of the primary time constant for the DC component in the fault current
[7 empty] | For the primary time constant tp | x: <= 400ms; x: :; (: a; +: =; Sr: 1
Factor for Function of the primary time constant for the DC component in the fault current
for a three phase fault at the set reach component in the fault current for of zone-1
[7 empty] | For the primary time constant tp | x: <= 200ms; x: :; (: k; +: =; Sr: 3
For Close-in faults:
[6 empty] | Since System tp |  |  |  | = | 127.2727 |  | ms, | a | = | 1
Ealreq = |  |  | 50000 |  | x | 1 |  | x | 1 | x | ( | 4 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
[6 empty] | 600 | [10 empty] | x | 1 | bar: Sr
|  | = | 426.4185 |  | V
For Endzone-1 3-ph faults:
|  |  |  | Since 3-ph tp for this fault | [5 empty] | = | 111.098 |  | ms, | k | = | 3
Ealreq = |  |  | 48271.7306 |  | x | 1 |  | x | 3 | x | ( | 4 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | 600 | [10 empty] | x | 1 | bar: Sr
|  | = | 1235.0376 |  | V
For Endzone-1 1-ph faults:
|  |  |  | Since 1-ph tp for this fault | [5 empty] | = | 86.3428 |  | ms, | k | = | 3
Ealreq = |  |  | 48587.1707 |  | x | 1 |  | x | 3 | x | ( | 4 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | 600 | [10 empty] | x | 1 | bar: Sr
|  | = | 1243.1082 |  | V
Hence, highest Ealreq for Differential & Distance functions at | [7 empty] | Rct: 600; Rl: A Tap =; Sr: 1243.1082 |  | V
Therefore, the required knee point voltage of the CT.
(Vk in terms of Ealreq as per the Manufacturer )
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: 1243.1082 |  | x | 0.8
[8 empty] | +: =; Sr: 994.4866 |  | V
|  |  | Available Vk |  |  | > | Required Vk | [14 empty] | <
|  |  |  | 800 |  | > | 994.4866
[5 empty] | Hence CT is: |  | Under Dimensioned | [14 empty] | Suitably Dimensioned
C. CT ADEQUECY CHECK FOR BREAKER FAILURE FUNCTION:
The CTs must have a rated equivalent secondary e.m.f. Eal that is larger than the maximum of the required secondary em.f. Ealreq as per below equation (1) (Refer : Annexure-G)
Ealreq = |  |  | 5 | x | Iop |  | x | Isr |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[8 empty] | x: Ipr; Sr: Ir | x | Ir
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipr; Sr: = | 600 |  | A
| Primary operate current | [6 empty] | +: Iop; Sr: = | 50000 |  | A
| CT secondary rated current | [6 empty] | +: Isr; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | 4 |  | W
| Total Lead Resistance | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of REQ 650 Relay | [15 empty] | 0 |  | VA | bar: + to Sr
| CT Iopernal Burden |  |  |  | PE = | Rct | x | x: Isr; k: x; x: Isr; +: PE; Sr: = | 4 |  | VA
| Rated CT Burden | [15 empty] | 994.4866 |  | VA | bar: + to Sr
| Rated ALF | [15 empty] | 0 | bar: + to Sr
Ealreq = |  |  | 5 | x | 50000 |  | x | 1 |  | x | ( | 4 | + | 1.097 | + | 0 |  |  | ) | ---(1)
[8 empty] | x: 600; Sr: 1 | x | 1
|  | = | 2123.7594 |  | V
Therefore, the required knee point voltage of the CT.
(Vk in terms of Ealreq as per the Manufacturer Refer Annexure-B)
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: 2123.7594 |  | x | 0.8
[8 empty] | +: =; Sr: 1699.0075 |  | V
|  |  | Available Vk |  |  | < | Required Vk
|  |  |  | 800 |  | < | 1699.0075
[5 empty] | Hence CT is: |  | Under Dimensioned
| T1 |  | Core1 |  | 0 |  | (Diff. + Dist.) | [10 empty] | Connected devices: | RED670
| 0 | [17 empty] | 0
[7 empty] | Tap-1 | k: Tap-2; (: Tap-3 |  |  | 0
| CT Ratio: | [5 empty] | 600 | k: -; (: -; +: /; Rl: 1; +: A
Class of Accuracy: | bar: k to x
| CT Resistance: | [6 empty] | x: Rct<; k: 3; (: W
| Knee Point Voltage: | [6 empty] | x: Vk>; k: 200; (: V |  |  |  |  | Highest Vk required = |  | #VALUE!
| Magnetizing Current: | [6 empty] | x: I0<; k: 100; (: mA at Vk
Other Burdens on same CT core:
| Burden of |  | RED670 |  |  |  | Sr' | x: =; k: 0.02; (: VA; +: Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | x: =; k: 0; (: VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1.097 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.097 |  | VA |  | =: =; Sl: 1.097; Isn: W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer.
For Close-in faults:
Ealreq = |  |  |  |  | Ikmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
For Through faults:
Ealreq = |  |  | 2 | x | Itmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: -; Isn: A
| Max. primary fundamental frequency fault current for close-in faults | [11 empty] | Sl: Ikmax; / (: =; Isn: 50000; Isn: A
| Max. primary fundamental frequency fault current for through fault | [13 empty] | Itmax | = | 47858.0776 |  | A | 3-phase
[16 empty] | = | 48245.339 |  | A | 1-phase
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: 3; Isn: W
| Lead Resistance of the current loop from the CT to Relay | [11 empty] | Sl: Rl; / (: =; Isn: 1.097; Isn: W
| Burden of RED 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
For Close-in faults:
Ealreq = |  |  |  |  | 50000 |  | x | 1 |  | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
- | bar: / ( to x
|  | = | #VALUE! |  | V
For Through faults (3-ph):
Ealreq = |  |  | 2 | x | 47858.0776 |  | x | 1 |  | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
For Through faults (1-ph):
Ealreq = |  |  | 2 | x | 48245.339 |  | x | 1 |  | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer. Ref Annexure-B
For Close-in faults:
Ealreq = |  |  | Ikmax |  | x | Isn |  | x | a | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
For Endzone-1 faults:
Ealreq = |  |  | Ikzone-1 |  | x | Isn |  | x | k | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipn; Sr: = | - |  | A
| Max. primary fundamental frequency fault current for close-in faults | [6 empty] | +: Ikmax; Sr: = | 50000 |  | A
| Max. primary fundamental frequency fault current for zone-1 faults | [6 empty] | +: Ikzone-1; Sr: = | 48271.7306 |  | A | 3-phase
[17 empty] | 48587.1707 |  | A | 1-phase | bar: Sr
| CT secondary rated current . | [6 empty] | +: Isn; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | 3 |  | W
| Lead resistance between relay and CT sec. Terminals (2 way ) | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of RED 670 Relay | [15 empty] | 0.02 |  | VA | bar: + to Sr
High Speed Distance : Quadrilateral Characteristic
Factor for the Function of the primary time constant for the DC component in the fault current
[7 empty] | For the primary time constant tp | x: <= 400ms; x: :; (: a; +: =; Sr: 1
Factor for Function of the primary time constant for the DC component in the fault current
for a three phase fault at the set reach component in the fault current for of zone-1
[7 empty] | For the primary time constant tp | x: <= 200ms; x: :; (: k; +: =; Sr: 3
For Close-in faults:
[6 empty] | Since System tp |  |  |  | = | 127.2727 |  | ms, | a | = | 1
Ealreq = |  |  | 50000 |  | x | 1 |  | x | 1 | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
For Endzone-1 3-ph faults:
|  |  |  | Since 3-ph tp for this fault | [5 empty] | = | 111.098 |  | ms, | k | = | 3
Ealreq = |  |  | 48271.7306 |  | x | 1 |  | x | 3 | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
For Endzone-1 1-ph faults:
|  |  |  | Since 1-ph tp for this fault | [5 empty] | = | 86.3428 |  | ms, | k | = | 3
Ealreq = |  |  | 48587.1707 |  | x | 1 |  | x | 3 | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
Hence, highest Ealreq for Differential & Distance functions at | [7 empty] | Rct: -; Rl: A Tap =; Sr: #VALUE! |  | V
Therefore, the required knee point voltage of the CT.
(Vk in terms of Ealreq as per the Manufacturer )
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: #VALUE! |  | x | 0.8
[8 empty] | +: =; Sr: #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | Required Vk
|  |  |  | 200 |  | #VALUE! | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
| T1 |  | Core1 |  | 0 |  | (Diff. + Dist.) | [10 empty] | Connected devices: | RED670
| 0 | [17 empty] | 0
[7 empty] | Tap-1 | k: Tap-2; (: Tap-3 |  |  | 0
| CT Ratio: | [5 empty] | 600 | k: -; (: -; +: /; Rl: 1; +: A
Class of Accuracy: | bar: (
| CT Resistance: | [6 empty] | x: Rct<; (: -; +: W
| Knee Point Voltage: | [6 empty] | x: Vk>; (: -; +: V |  |  |  |  | Highest Vk required = |  | #VALUE!
| Magnetizing Current: | [6 empty] | x: I0<; (: -; +: mA at Vk
Other Burdens on same CT core:
| Burden of |  | RED670 |  |  |  | Sr' | x: =; k: 0.02; (: VA; +: Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | x: =; k: 0; (: VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.077 |  | VA |  | =: =; Sl: 1.077; Isn: W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer. Ref Annexure-B
For Close-in faults:
Ealreq = |  |  |  |  | Ikmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
For Through faults:
Ealreq = |  |  | 2 | x | Itmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: -; Isn: A
| Max. primary fundamental frequency fault current for close-in faults | [11 empty] | Sl: Ikmax; / (: =; Isn: 50000; Isn: A
| Max. primary fundamental frequency fault current for through fault | [13 empty] | Itmax | = | 47858.0776 |  | A | 3-phase
[16 empty] | = | 48245.339 |  | A | 1-phase
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: -; Isn: W
| Lead Resistance of the current loop from the CT to Relay | [11 empty] | Sl: Rl; / (: =; Isn: 1.097; Isn: W
| Burden of RED 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
For Close-in faults:
Ealreq = |  |  |  |  | 50000 |  | x | 1 |  | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
- | bar: / ( to x
|  | = | #VALUE! |  | V
For Through faults (3-ph):
Ealreq = |  |  | 2 | x | 47858.0776 |  | x | 1 |  | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
For Through faults (1-ph):
Ealreq = |  |  | 2 | x | 48245.339 |  | x | 1 |  | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer. Ref Annexure-B
For Close-in faults:
Ealreq = |  |  | Ikmax |  | x | Isn |  | x | a | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
For Endzone-1 faults:
Ealreq = |  |  | Ikzone-1 |  | x | Isn |  | x | k | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipn; Sr: = | - |  | A
| Max. primary fundamental frequency fault current for close-in faults | [6 empty] | +: Ikmax; Sr: = | 50000 |  | A
| Max. primary fundamental frequency fault current for zone-1 faults | [6 empty] | +: Ikzone-1; Sr: = | 48271.7306 |  | A | 3-phase
[17 empty] | 48587.1707 |  | A | 1-phase | bar: Sr
| CT secondary rated current . | [6 empty] | +: Isn; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | - |  | W
| Lead resistance between relay and CT sec. Terminals (2 way ) | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of RED 670 Relay | [15 empty] | 0.02 |  | VA | bar: + to Sr
High Speed Distance : Quadrilateral Characteristic
Factor for the Function of the primary time constant for the DC component in the fault current
[7 empty] | For the primary time constant tp | x: <= 400ms; x: :; (: a; +: =; Sr: 1
Factor for Function of the primary time constant for the DC component in the fault current
for a three phase fault at the set reach component in the fault current for of zone-1
[7 empty] | For the primary time constant tp | x: <= 200ms; x: :; (: k; +: =; Sr: 3
For Close-in faults:
[6 empty] | Since System tp |  |  |  | = | 127.2727 |  | ms, | a | = | 1
Ealreq = |  |  | 50000 |  | x | 1 |  | x | 1 | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
For Endzone-1 3-ph faults:
|  |  |  | Since 3-ph tp for this fault | [5 empty] | = | 111.098 |  | ms, | k | = | 3
Ealreq = |  |  | 48271.7306 |  | x | 1 |  | x | 3 | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
For Endzone-1 1-ph faults:
|  |  |  | Since 1-ph tp for this fault | [5 empty] | = | 86.3428 |  | ms, | k | = | 0
Ealreq = |  |  | 48587.1707 |  | x | 1 |  | x | 0 | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
Hence, highest Ealreq for Differential & Distance functions at | [7 empty] | Rct: -; Rl: A Tap =; Sr: #VALUE! |  | V
Therefore, the required knee point voltage of the CT.
(Summary of CT requirements for ABB relays, February 2008, formula no. 29, page 17/18)
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: #VALUE! |  | x | 0.8
[8 empty] | +: =; Sr: #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | Required Vk
|  |  |  | - |  | #VALUE! | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | x: Class; x: CT Resistance (W) @ 75OC; Rct: Limiting Secondary Voltage (Ual), V; Rl: Mag. Current (Io), mA at Vk; Sr: Relay / Instrument Type |  | CT Suitability
T1 | Core1 |  | 600 |  | 1 | 120 | 6 | x: PX; x: 4; Rct: 800; Rl: 50; Sr: RED670 |  | Under Dimensioned
|  |  | - | [14 empty] | - | bar: x; Rct; Rl
|  |  | - | [14 empty] | - | bar: x; Rct; Rl

## RET670_650-PX (HV) (2) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV Incomer Transformer Feeder | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core1 |  |  |  | (Transformer Differential) | [10 empty] | Connected devices: | RET670 |  | Note: CT requirements for other protection functions are different, pl. refer to the Application Manual.
Note: CT requirements mentioned here are applicable for solidly earthed neutral system. For impedance earthed system, pl. refer to the Application manual
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [9 empty] | Note: CT requirements are similar for REG670 / 650 relay.
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX
| CT Resistance: |  |  |  |  | Rct < | 10 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 400 |  | V | [11 empty] | Highest Vk required = |  |  |  | 186.7176
| Magnetizing Current: |  |  |  |  | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | RET670 |  |  |  | Sr' | = | 0.02 |  | VA |  | Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [5 empty] | Sl' | = | 1.077 |  | VA |  |  | = | 1.097 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.097 |  | VA |  | =: =; Sl: 1.097; Isn: W
Power Transformer Data:
| Power Rating | [11 empty] | =: =; Sl: 100; Isn: MVA
| Percentage Impedance | [11 empty] | =: =; Sl: 25; Isn: %
| HV Rated Voltage, | [11 empty] | Rl: Un1; =: =; Sl: 33; Isn: kV
| Transformer Full load current | [5 empty] | Int | = | MVA |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: Un1
[8 empty] | = | 100 |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: 33
[8 empty] | = | 1749.5463 |  | A
| Maximum through Fault Current (LV Side) | [10 empty] | Itf | Rl: =; =: Int; / (: /; Isn: Percentage Impedance
[13 empty] | = | 1749.5463 |  | / | 0.25
[12 empty] | Itf | Rl: =; =: 6998.1851; / (: A
The CTs must have a rated equivalent secondary e.m.f. Eal that is larger than the maximum of the required secondary em.f. Ealreq below equation (1) and (2):
(Refer : Annexure-B)
Ealreq = |  |  | 30 | x | Int |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
Ealreq = |  |  | 2 | x | Itf |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
In substations with breaker-and-a-half or double-busbar double-breaker arrangement, the fault current may pass two main CTs for the transformer differential protection without passing the power transformer. In such cases and if both main CTs have equal ratios and magnetization characteristics the CTs must satisfy equation (1) and (3):
Ealreq = |  |  |  |  | If |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(3)
Ipn | bar: / ( to x
[7 empty] | Equation (3) applicable ? |  |  |  |  | N | bar: Rl
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: 2500; Isn: A
| Rated Primary current of Transformer | [11 empty] | Sl: Int; / (: =; Isn: 1749.5463; Isn: A
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: Itf; / (: =; Isn: 6998.1851; Isn: A
- main CTs and the power transformer
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: If; / (: =; Isn: -; Isn: A
- main CTs without passing the power transformer:
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: 10; Isn: W
| Total Lead Resistance + other reisistance connected to the core | [11 empty] | Sl: Rl; / (: =; Isn: 1.097; Isn: W
| Burden of RET 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
Ealreq = |  |  | 30 | x | 1749.5463 |  | x | 1 |  | x | ( | 10 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
2500 | bar: / ( to x
|  | = | 233.3969 |  | V
Ealreq = |  |  | 2 | x | 6998.1851 |  | x | 1 |  | x | ( | 10 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
2500 | bar: / ( to x
|  | = | 62.2392 |  | V
Ealreq = |  |  |  |  | - |  | x | 1 |  | x | ( | 10 | + | 1.097 | + | 0.02 |  |  | ) | ---(3)
2500 | bar: / ( to x
|  | = | #VALUE! |  | V | * | Not applicable
Hence, highest Eal for Differential functions at | [11 empty] | 2500 | =: A Tap =; / (: 233.3969; x: V
Therefore, the required knee point voltage of the CT.
(Vk in terms of Ealreq as per the Manufacturer Refer Annexure-B)
[14 empty] | Vk | = | Ealreq |  | x | 0.8
[15 empty] | = | 233.3969 |  | x | 0.8
[15 empty] | = | 186.7176 |  | V
|  |  | Available Vk |  |  | > | Required Vk
|  |  |  | 400 |  | > | 186.7176
[5 empty] | Hence CT is: |  | Suitable Dimensions
| T1 |  | Core1 |  |  |  | (Transformer Differential) | [5 empty] | x: Connected devices:; Isn: RET670
| 0 | [11 empty] | Isn: 0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 |  | Isn: 0
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | Rl: /; =: 1; Sl: A
| Class of Accuracy: | [7 empty] | PX
| CT Resistance: | [6 empty] | Rct< | 6 |  | W
| Knee Point Voltage: | [6 empty] | Vk> | 500 |  | V | [9 empty] | Highest Vk required = |  |  |  | #VALUE!
| Magnetizing Current: | [6 empty] | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | RET670 |  |  |  | Sr' | = | 0.02 |  | VA |  | Rl: Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [5 empty] | Sl' | = | 1.077 |  | VA |  |  | = | 1.097 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.097 |  | VA |  | =: =; Sl: 1.097; Isn: W
Power Transformer Data:
| Power Rating | [11 empty] | =: =; Sl: 100; Isn: MVA
| Percentage Impedance | [11 empty] | =: =; Sl: 25; Isn: %
| HV Rated Voltage, | [11 empty] | Rl: Un1; =: =; Sl: 33; Isn: kV
| Transformer Full load current | [5 empty] | Int | = | MVA |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: Un1
[8 empty] | = | 100 |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: 33
[8 empty] | = | 1749.5463 |  | A
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
| Maximum through Fault Current (LV Side) | [10 empty] | Itf | Rl: =; =: Int; / (: x; Isn: 16
[13 empty] | = | 1749.5463 |  | x | 16
[12 empty] | Itf | Rl: =; =: 27992.7403; / (: A |  |  |  | 9.3309
The CTs must have a rated equivalent secondary e.m.f. Eal that is larger than the maximum of the required secondary em.f. Ealreq below equation (1) and (2): | [21 empty] | (Refer : Annexure-B)
Ealreq = |  |  | 30 | x | Int |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
Ealreq = |  |  | 2 | x | Itf |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
In substations with breaker-and-a-half or double-busbar double-breaker arrangement, the fault current may pass two main CTs for the transformer differential protection without passing the power transformer. In such cases and if both main CTs have equal ratios and magnetization characteristics the CTs must satisfy equation (1) and (3):
Ealreq = |  |  |  |  | If |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(3)
Ipn | bar: / ( to x
[7 empty] | Equation (3) applicable ? |  |  |  |  | N
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: -; Isn: A
| Rated Primary current of Transformer | [11 empty] | Sl: Int; / (: =; Isn: 1749.5463; Isn: A
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: Itf; / (: =; Isn: 27992.7403; Isn: A
- main CTs and the power transformer
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: If; / (: =; Isn: -; Isn: A
- main CTs without passing the power transformer:
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: 6; Isn: W
| Total Lead Resistance + other reisistance connected to the core | [11 empty] | Sl: Rl; / (: =; Isn: 1.097; Isn: W
| Burden of RET 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
Ealreq = |  |  | 30 | x | 1749.5463 |  | x | 1 |  | x | ( | 6 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
- | bar: / ( to x
|  | = | #VALUE! |  | V
Ealreq = |  |  | 2 | x | 27992.7403 |  | x | 1 |  | x | ( | 6 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
Ealreq = |  |  |  |  | - |  | x | 1 |  | x | ( | 6 | + | 1.097 | + | 0.02 |  |  | ) | ---(3)
- | bar: / ( to x
|  | = | #VALUE! |  | V | * | Not applicable
Hence, highest Eal for Differential functions at | [11 empty] | - | =: A Tap =; / (: #VALUE!; x: V
Therefore, the required knee point voltage of the CT.
(Vk in terms of Ealreq as per the Manufacturer Refer Annexure-B)
[14 empty] | Vk | = | Ealreq |  | x | 0.8
[15 empty] | = | #VALUE! |  | x | 0.8
[15 empty] | = | #VALUE! |  | V
|  |  | Available Vk |  |  | > | Required Vk
|  |  |  | 500 |  | > | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
| T1 |  | Core1 |  | HV side |  | (Transformer Differential) | [5 empty] | x: Connected devices:; Isn: RET670
| 0 | [11 empty] | Isn: 0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 |  | Isn: 0
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | Rl: /; =: 1; Sl: A
| Class of Accuracy: | [9 empty] | PX
| CT Resistance: | [8 empty] | Rct< | - | bar: Rl
| Knee Point Voltage: | [8 empty] | Vk> | - | [9 empty] | Highest Vk required = |  |  |  | #VALUE! | bar: Rl
| Magnetizing Current: | [8 empty] | I0< | - |  | Rl: mA at Vk
Other Burdens on same CT core:
| Burden of |  | RET670 |  |  |  | Sr' | = | 0.02 |  | VA |  | Rl: Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [5 empty] | Sl' | = | 1.077 |  | VA |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.077 |  | VA |  | =: =; Sl: 1.077; Isn: W
Power Transformer Data:
| Power Rating | [11 empty] | =: =; Sl: 100; Isn: MVA
| Percentage Impedance | [11 empty] | =: =; Sl: 25; Isn: %
| HV Rated Voltage, | [11 empty] | Rl: Un1; =: =; Sl: 33; Isn: kV
| Transformer Full load current | [5 empty] | Int | = | MVA |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: Un1
[8 empty] | = | 100 |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: 33
[8 empty] | = | 1749.5463 |  | A
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
| Maximum through Fault Current (HV Side) | [10 empty] | Itf | Rl: =; =: Int; / (: x; Isn: 16
[13 empty] | = | 1749.5463 |  | x | 16
[12 empty] | Itf | Rl: =; =: 27992.7403; / (: A
The CTs must have a rated equivalent secondary e.m.f. Eal that is larger than the maximum of the required secondary em.f. Ealreq below equation (1) and (2):
Ealreq = |  |  | 30 | x | Int |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
Ealreq = |  |  | 2 | x | Itf |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
In substations with breaker-and-a-half or double-busbar double-breaker arrangement, the fault current may pass two main CTs for the transformer differential protection without passing the power transformer. In such cases and if both main CTs have equal ratios and magnetization characteristics the CTs must satisfy equation (1) and (3):
Ealreq = |  |  |  |  | If |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(3)
Ipn | bar: / ( to x
[7 empty] | Equation (3) applicable ? |  |  |  |  | N
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: -; Isn: A
| Rated Primary current of Transformer | [11 empty] | Sl: Int; / (: =; Isn: 1749.5463; Isn: A
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: Itf; / (: =; Isn: 27992.7403; Isn: A
- main CTs and the power transformer
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: If; / (: =; Isn: -; Isn: A
- main CTs without passing the power transformer:
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: -; Isn: W
| Total Lead Resistance + other reisistance connected to the core | [11 empty] | Sl: Rl; / (: =; Isn: 1.077; Isn: W
| Burden of RED 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
Ealreq = |  |  | 30 | x | 1749.5463 |  | x | 1 |  | x | ( | - | + | 1.077 | + | 0.02 |  |  | ) | ---(1)
- | bar: / ( to x
|  | = | #VALUE! |  | V
Ealreq = |  |  | 2 | x | 27992.7403 |  | x | 1 |  | x | ( | - | + | 1.077 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
Ealreq = |  |  |  |  | - |  | x | 1 |  | x | ( | - | + | 1.077 | + | 0.02 |  |  | ) | ---(3)
- | bar: / ( to x
|  | = | #VALUE! |  | V | * | Not applicable
Hence, highest Eal for Differential + REF functions at | [11 empty] | - | =: A Tap =; / (: #VALUE!; x: V
Therefore, the required knee point voltage of the CT.
(Summary of CT requirements for ABB relays, February 2008, formula no. 29, page 17/18)
[14 empty] | Vk | = | Ealreq |  | x | 0.8
[15 empty] | = | #VALUE! |  | x | 0.8
[15 empty] | = | #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | Required Vk
|  |  |  | - |  | #VALUE! | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | CT Resistance (W) @ 75OC |  | Limiting Secondary Voltage (Ual), V | =: Mag. Current (Io), mA at Vk; / (: Relay / Instrument Type; x: CT Suitability
T1 | Core1 |  | 2500 |  | 1 | 120 | 6 | PX |  | 10 |  | 400 | =: 50; / (: RET670; x: Suitable Dimensions
|  |  | - | [6 empty] | - |  | - | bar: =; x
|  |  | - | [6 empty] | - |  | - | bar: =; x
HITACHI | [6 empty] | CT / VT | [5 empty] | =: Contract No.; Isn: N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [5 empty] | =: Date; Isn: 46106
0 | [6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [5 empty] | =: Document No.; Isn: -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV Incomer Transformer Feeder | [5 empty] | =: Contractor; Isn: HITACHI
| BCT13,14,15 |  | Core2 |  | LV side |  | (Transformer Differential) | [5 empty] | x: Connected devices:; Isn: RET670
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | bar: Isn to )
| CT Ratio: | [5 empty] | 1200 |  | - |  | - |  | Rl: /; =: 1; Sl: A
| Class of Accuracy: | [5 empty] | TPS
| CT Resistance: |  |  |  |  | Rct < | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Ual > | 430 |  | V | [11 empty] | Highest Vk required = |  |  |  | 56.8908
| Magnetizing Current: |  |  |  |  | I0< | 20 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | RET670 |  |  |  | Sr' | = | 0.02 |  | VA |  | Rl: Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [5 empty] | Sl' | = | 1.077 |  | VA |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.077 |  | VA |  | =: =; Sl: 1.077; Isn: W
Power Transformer Data:
| Power Rating | [11 empty] | =: =; Sl: 100; Isn: MVA
| Percentage Impedance | [11 empty] | =: =; Sl: 25; Isn: %; Isn: **
| HV Rated Voltage, | [11 empty] | Rl: Un1; =: =; Sl: 132; Isn: kV
| Transformer Full load current | [5 empty] | Int | = | MVA |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: Un1
[8 empty] | = | 100 |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: 132
[8 empty] | = | 437.3866 |  | A
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
| Maximum through Fault Current (LV Side) | [10 empty] | Itf | Rl: =; =: Int; / (: x; Isn: 16
[13 empty] | = | 437.3866 |  | x | 16
[12 empty] | Itf | Rl: =; =: 6998.1851; / (: A
The CTs must have a rated equivalent secondary e.m.f. Eal that is larger than the maximum of the required secondary em.f. Ealreq below equation (1) and (2): (Refer : Annexure-B)
[8 empty] | ** | Assumed
Ealreq = |  |  | 30 | x | Int |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
Ealreq = |  |  | 2 | x | Itf |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
In substations with breaker-and-a-half or double-busbar double-breaker arrangement, the fault current may pass two main CTs for the transformer differential protection without passing the power transformer. In such cases and if both main CTs have equal ratios and magnetization characteristics the CTs must satisfy equation (1) and (3):
Ealreq = |  |  |  |  | If |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(3)
Ipn | bar: / ( to x
[7 empty] | Equation (3) applicable ? |  |  |  |  | N | bar: Rl
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: 1200; Isn: A
| Rated Primary current of Transformer | [11 empty] | Sl: Int; / (: =; Isn: 437.3866; Isn: A
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: Itf; / (: =; Isn: 6998.1851; Isn: A
- main CTs and the power transformer
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: If; / (: =; Isn: -; Isn: A
- main CTs without passing the power transformer:
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: 5; Isn: W
| Total Lead Resistance + other reisistance connected to the core | [11 empty] | Sl: Rl; / (: =; Isn: 1.077; Isn: W
| Burden of RED 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
Ealreq = |  |  | 30 | x | 437.3866 |  | x | 1 |  | x | ( | 5 | + | 1.077 | + | 0.02 |  |  | ) | ---(1)
1200 | bar: / ( to x
|  | = | 66.6689 |  | V
Ealreq = |  |  | 2 | x | 6998.1851 |  | x | 1 |  | x | ( | 5 | + | 1.077 | + | 0.02 |  |  | ) | ---(2)
1200 | bar: / ( to x
|  | = | 71.1135 |  | V
Ealreq = |  |  |  |  | - |  | x | 1 |  | x | ( | 5 | + | 1.077 | + | 0.02 |  |  | ) | ---(3)
1200 | bar: / ( to x
|  | = | #VALUE! |  | V | * | Not applicable
Hence, highest Eal for Differential functions at | [11 empty] | 1200 | =: A Tap =; / (: 71.1135; x: V
Therefore, the required knee point voltage of the CT.
(Ual in terms of Ealreq as per the Manufacturer Refer Annexure-B)
[14 empty] | Vk | = | Ealreq |  | x | 0.8
[15 empty] | = | 71.1135 |  | x | 0.8
[15 empty] | = | 56.8908 |  | V
|  |  | Available Ual |  |  | > | Required Ual
|  |  |  | 430 |  | > | 56.8908
[5 empty] | Hence CT is: |  | Suitably Dimensioned
| BCT13,14,15 |  | Core2 |  | LV side |  | (Transformer Differential) | [5 empty] | x: Connected devices:; Isn: RET670
| 0 | [11 empty] | Isn: 0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 |  | Isn: 0
| CT Ratio: | [5 empty] | 1200 |  | - |  | - |  | Rl: /; =: 1; Sl: A
| Class of Accuracy: | [7 empty] | TPS
| CT Resistance: | [6 empty] | Rct< | - |  | W
| Knee Point Voltage: | [6 empty] | Vk> | - |  | V | [9 empty] | Highest Vk required = |  |  |  | #VALUE!
| Magnetizing Current: | [6 empty] | I0< | - |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | RET670 |  |  |  | Sr' | = | 0.02 |  | VA |  | Rl: Lead + Other resisitance connected
| Burden of |  | 0 | [5 empty] | 0 |  | VA
| Burden of |  | 0 | [5 empty] | 0 |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [5 empty] | Sl' | = | 1.077 |  | VA |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.077 |  | VA |  | =: =; Sl: 1.077; Isn: W
Power Transformer Data:
| Power Rating | [11 empty] | =: =; Sl: 100; Isn: MVA
| Percentage Impedance | [11 empty] | =: =; Sl: 25; Isn: %
| HV Rated Voltage, | [11 empty] | Rl: In1; =: =; Sl: 132; Isn: kV
| Transformer Full load current | [5 empty] | Int | = | MVA |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: Un1
[8 empty] | = | 100 |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: 132
[8 empty] | = | 437.3866 |  | A
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
| Maximum through Fault Current (LV Side) | [10 empty] | Itf | Rl: =; =: Int; / (: x; Isn: 16
[13 empty] | = | 437.3866 |  | x | 16
[12 empty] | Itf | Rl: =; =: 6998.1851; / (: A
The CTs must have a rated equivalent secondary e.m.f. Eal that is larger than the maximum of the required secondary em.f. Ealreq below equation (1) and (2):
Ealreq = |  |  | 30 | x | Int |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
Ealreq = |  |  | 2 | x | Itf |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
In substations with breaker-and-a-half or double-busbar double-breaker arrangement, the fault current may pass two main CTs for the transformer differential protection without passing the power transformer. In such cases and if both main CTs have equal ratios and magnetization characteristics the CTs must satisfy equation (1) and (3):
Ealreq = |  |  |  |  | If |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(3)
Ipn | bar: / ( to x
[7 empty] | Equation (3) applicable ? |  |  |  |  | N
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: -; Isn: A
| Rated Primary current of Transformer | [11 empty] | Sl: Int; / (: =; Isn: 437.3866; Isn: A
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: Itf; / (: =; Isn: 6998.1851; Isn: A
- main CTs and the power transformer
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: If; / (: =; Isn: -; Isn: A
- main CTs without passing the power transformer: (Bus fault level / 2)
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: -; Isn: W
| Total Lead Resistance + other reisistance connected to the core | [11 empty] | Sl: Rl; / (: =; Isn: 1.077; Isn: W
| Burden of RED 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
Ealreq = |  |  | 30 | x | 437.3866 |  | x | 1 |  | x | ( | - | + | 1.077 | + | 0.02 |  |  | ) | ---(1)
- | bar: / ( to x
|  | = | #VALUE! |  | V
Ealreq = |  |  | 2 | x | 6998.1851 |  | x | 1 |  | x | ( | - | + | 1.077 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
Ealreq = |  |  |  |  | - |  | x | 1 |  | x | ( | - | + | 1.077 | + | 0.02 |  |  | ) | ---(3)
- | bar: / ( to x
|  | = | #VALUE! |  | V | * | Not applicable
Hence, highest Eal for Differential + REF functions at | [11 empty] | - | =: A Tap =; / (: #VALUE!; x: V
Therefore, the required knee point voltage of the CT.
(Summary of CT requirements for ABB relays, February 2008, formula no. 29, page 17/18)
[14 empty] | Vk | = | Ealreq |  | x | 0.8
[15 empty] | = | #VALUE! |  | x | 0.8
[15 empty] | = | #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | Required Vk
|  |  |  | - |  | #VALUE! | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
| BCT13,14,15 |  | Core2 |  | LV side |  | (Transformer Differential) | [5 empty] | x: Connected devices:; Isn: RET670
| 0 | [11 empty] | Isn: 0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 |  | Isn: 0
| CT Ratio: | [5 empty] | 1200 |  | - |  | - |  | Rl: /; =: 1; Sl: A
| Class of Accuracy: | [9 empty] | TPS
| CT Resistance: | [8 empty] | Rct< | - | bar: Rl
| Knee Point Voltage: | [8 empty] | Vk> | - | [9 empty] | Highest Vk required = |  |  |  | #VALUE! | bar: Rl
| Magnetizing Current: | [8 empty] | I0< | - |  | Rl: mA at Vk
Other Burdens on same CT core:
| Burden of |  | RET670 |  |  |  | Sr' | = | 0.02 |  | VA |  | Rl: Lead + Other resisitance connected
| Burden of |  | 0 | [5 empty] | 0 |  | VA
| Burden of |  | 0 | [5 empty] | 0 |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [5 empty] | Sl' | = | 1.077 |  | VA |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.077 |  | VA |  | =: =; Sl: 1.077; Isn: W
Power Transformer Data:
| Power Rating | [11 empty] | =: =; Sl: 100; Isn: MVA
| Percentage Impedance | [11 empty] | =: =; Sl: 25; Isn: %
| HV Rated Voltage, | [11 empty] | Rl: Un1; =: =; Sl: 132; Isn: kV
| Transformer Full load current | [5 empty] | Int | = | MVA |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: Un1
[8 empty] | = | 100 |  | x | 1000 | Rl: /; =: √3; Sl: x; / (: 132
[8 empty] | = | 437.3866 |  | A
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
| Maximum through Fault Current (LV Side) | [10 empty] | Itf | Rl: =; =: Int; / (: x; Isn: 16
[13 empty] | = | 437.3866 |  | x | 16
[12 empty] | Itf | Rl: =; =: 6998.1851; / (: A
The CTs must have a rated equivalent secondary e.m.f. Eal that is larger than the maximum of the required secondary em.f. Ealreq below equation (1) and (2):
Ealreq = |  |  | 30 | x | Int |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
Ealreq = |  |  | 2 | x | Itf |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
In substations with breaker-and-a-half or double-busbar double-breaker arrangement, the fault current may pass two main CTs for the transformer differential protection without passing the power transformer. In such cases and if both main CTs have equal ratios and magnetization characteristics the CTs must satisfy equation (1) and (3):
Ealreq = |  |  |  |  | If |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(3)
Ipn | bar: / ( to x
[7 empty] | Equation (3) applicable ? |  |  |  |  | N
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: -; Isn: A
| Rated Primary current of Transformer | [11 empty] | Sl: Int; / (: =; Isn: 437.3866; Isn: A
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: Itf; / (: =; Isn: 6998.1851; Isn: A
- main CTs and the power transformer
| Max. primary fundamental frequency current that passes through two - | [11 empty] | Sl: If; / (: =; Isn: -; Isn: A
- main CTs without passing the power transformer: (Bus fault level / 2)
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: -; Isn: W
| Total Lead Resistance + other reisistance connected to the core | [11 empty] | Sl: Rl; / (: =; Isn: 1.077; Isn: W
| Burden of RED 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
Ealreq = |  |  | 30 | x | 437.3866 |  | x | 1 |  | x | ( | - | + | 1.077 | + | 0.02 |  |  | ) | ---(1)
- | bar: / ( to x
|  | = | #VALUE! |  | V
Ealreq = |  |  | 2 | x | 6998.1851 |  | x | 1 |  | x | ( | - | + | 1.077 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
Ealreq = |  |  |  |  | - |  | x | 1 |  | x | ( | - | + | 1.077 | + | 0.02 |  |  | ) | ---(3)
- | bar: / ( to x
|  | = | #VALUE! |  | V | * | Not applicable
Hence, highest Eal for Differential + REF functions at | [11 empty] | - | =: A Tap =; / (: #VALUE!; x: V
Therefore, the required knee point voltage of the CT.
(Summary of CT requirements for ABB relays, February 2008, formula no. 29, page 17/18)
[14 empty] | Vk | = | Ealreq |  | x | 0.8
[15 empty] | = | #VALUE! |  | x | 0.8
[15 empty] | = | #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | Required Vk
|  |  |  | - |  | #VALUE! | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  |  | CT Cable m/mm2 |  | Class |  | CT Resistance (W) @ 75OC |  | Rl: CT Resistance (W) @ 75OC; =: Limiting Secondary Voltage (Ual), V; Isn: Mag. Current (Io), mA at Ual; ): Relay / Instrument Type
BCT13,14,15 | 0 | Core2 | 1200 | - | - | 1 | 120 | 6 | TPS |  | 5 | - | - | 430 | - | - | 20 | - | - | RET670
0 | 0
0 | CT Ratio:

## SEL487E-X (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV Side Trafo Feeder (100MVA) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core2 |  |  |  | (Transformer Differential) | [10 empty] | Connected devices: | SEL487E
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 3150 |  | 2000 |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX
| CT Resistance: |  |  |  |  | Rct< | 9 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 800 |  | V | [12 empty] | Highest Vk required = |  |  | 176.6733
| Magnetizing Current: |  |  |  |  | I0< | 30 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | SEL487E |  |  |  | Sr' | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Total lead burden | [5 empty] | Sl' | = | 0.74045 |  | VA
| Total lead + other burden | [5 empty] | Sl | = | 0.84045 |  | VA
| Resisitance of the relay: | [10 empty] | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 0.84045 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 0.84045 |  | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 33 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 33 | ) | bar: Resisitance of the relay: )
[9 empty] | 1749.5463 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (LV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 1749.5463 |  | x | 16
[12 empty] | Itf | = | 27992.7403 |  | A
Minimum required Knee point voltage | [23 empty] | (As per SEL guideline - Aug-2010)
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
| CT Primary Current | [13 empty] | Ipn |  | = | 3150 |  | A
| CT Internal Resistance | [13 empty] | Rct |  | = | 9 |  | W
| Burden of CT Leads | [13 empty] | Rl |  | = | 0.84045 |  | W
| Burden of the relay | [13 empty] | Rr |  | = | 0.1 |  | W
| Maximum through Fault Current on CT sec. | [13 empty] | If |  | = | 8.8866 |  | A
| Relay normal current | [13 empty] | Inrelay (Ir) |  | = | 1 |  | A
Minimum required Knee point voltage, hence,
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
|  | ³ | 2 | * | 8.8866 |  | * | ( | 9 | + | 0.84045 | + | 0.1 | )
|  | = | 176.6733 |  | V
|  |  | Available Vk |  |  | > | *: Required Vk
|  |  |  | 800 |  | > | *: 176.6733
[5 empty] | Hence CT is: |  | *: Suitable Dimensions
| T1 |  | Core2 |  |  |  | *: (Transformer Differential) |  |  |  | Connected devices: | SEL487E
| 0 | [17 empty] | 0
[7 empty] | *: Tap-1; Rct: Tap-2; Rl: Tap-3 |  |  |  |  | 0
| CT Ratio: | [5 empty] | 3150 |  | 2000 |  | - |  | / | 1 | A
Class of Accuracy: | bar: Rct to +
| CT Resistance: | [5 empty] | (: Rct<; Rct: 6; Rl: W
| Knee Point Voltage: | [5 empty] | (: Vk>; Rct: 500; Rl: V | [7 empty] | Highest Vk required = |  |  | 194.2823
| Magnetizing Current: | [5 empty] | (: I0<; Rct: 60; Rl: mA at Vk
Other Burdens on same CT core:
| Burden of |  | SEL487E |  |  |  | *: Sr'; (: =; Rct: 0.1; Rl: VA
| Burden of |  | 0 |  |  |  | (: =; Rct: 0; Rl: VA
| Burden of |  | 0 |  |  |  | (: =; Rct: 0; Rl: VA
| Total lead burden | [5 empty] | *: Sl'; (: =; Rct: 0.74045; Rl: VA
| Total lead + other burden | [5 empty] | *: Sl; (: =; Rct: 0.84045; Rl: VA
| Resisitance of the relay: | [5 empty] | +: Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 0.84045 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 0.84045 |  | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 33 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 33 | ) | bar: Resisitance of the relay: )
[9 empty] | 1749.5463 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (LV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 1749.5463 |  | x | 16
[12 empty] | Itf | = | 27992.7403 |  | A
Minimum required Knee point voltage | [22 empty] | (As per SEL guideline - Aug-2010)
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
| CT Primary Current | [13 empty] | Ipn |  | = | 2000 |  | A
| CT Internal Resistance | [13 empty] | Rct |  | = | 6 |  | W
| Burden of CT Leads | [13 empty] | Rl |  | = | 0.84045 |  | W
| Burden of the relay | [13 empty] | Rr |  | = | 0.1 |  | W
| Maximum through Fault Current on CT sec. | [13 empty] | If |  | = | 13.9964 |  | A
| Relay normal current | [13 empty] | Inrelay (Ir) |  | = | 1 |  | A
Minimum required Knee point voltage, hence,
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
|  | ³ | 2 | * | 13.9964 |  | * | ( | 6 | + | 0.84045 | + | 0.1 | )
|  | = | 194.2823 |  | V
|  |  | Available Vk |  |  | > | *: Required Vk
|  |  |  | 500 |  | > | *: 194.2823
[5 empty] | Hence CT is: |  | *: Suitable Dimensions
| T1 |  | Core2 |  | HV side |  | *: (Transformer Differential) |  |  |  | Connected devices: | SEL487E
| 0 | [17 empty] | 0
[7 empty] | *: Tap-1; Rct: Tap-2; Rl: Tap-3 |  |  |  |  | 0
| CT Ratio: | [5 empty] | 3150 |  | 2000 |  | - |  | / | 1 | A
Class of Accuracy: | bar: Rl
| CT Resistance: | [5 empty] | +: Rct<; Rl: 3; Rr: W
| Knee Point Voltage: | [5 empty] | +: Vk>; Rl: 200; Rr: V | [7 empty] | Highest Vk required = |  |  | #VALUE!
| Magnetizing Current: | [5 empty] | +: I0<; Rl: 50; Rr: mA at Vk
Other Burdens on same CT core:
| Burden of |  | SEL487E |  |  |  | *: Sr'; (: =; Rct: 0.1; Rl: VA
| Burden of |  | 0 |  |  |  | (: =; Rct: 0; Rl: VA
| Burden of |  | 0 |  |  |  | (: =; Rct: 0; Rl: VA
| Total lead burden | [5 empty] | *: Sl'; (: =; Rct: 0.74045; Rl: VA
| Total lead + other burden | [5 empty] | *: Sl; (: =; Rct: 0.74045; Rl: VA
| Resisitance of the relay: | [5 empty] | +: Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 0.74045 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 0.74045 |  | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 33 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 33 | ) | bar: Resisitance of the relay: )
[9 empty] | 1749.5463 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (HV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 1749.5463 |  | x | 16
[12 empty] | Itf | = | 27992.7403 |  | A
ABB
Minimum required Knee point voltage (As per SEL guideline - Aug-2010)
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
| CT Primary Current | [13 empty] | Ipn |  | = | - |  | A
| CT Internal Resistance | [13 empty] | Rct |  | = | 3 |  | W
| Burden of CT Leads | [13 empty] | Rl |  | = | 0.74045 |  | W
| Burden of the relay | [13 empty] | Rr |  | = | 0.1 |  | W
| Maximum through Fault Current on CT sec. | [13 empty] | If |  | = | #VALUE! |  | A
| Relay normal current | [13 empty] | Inrelay (Ir) |  | = | 1 |  | A
Minimum required Knee point voltage, hence,
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
|  | ³ | 2 | * | #VALUE! |  | * | ( | 3 | + | 0.74045 | + | 0.1 | )
|  | = | #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | *: Required Vk
|  |  |  | Sr' |  | #VALUE! | *: #VALUE!
[5 empty] | Hence CT is: |  | *: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 | (: Class; +: CT Resistance (W) @ 75OC; +: Limiting Secondary Voltage (Ual), V; ): Mag. Current (Io), mA at Vk |  | Relay / Instrument Type |  | CT Suitability
T1 | Core2 |  | 3150 |  | 1 | 120 | 6 | PX |  | 9 |  | 800 |  | 30 |  | SEL487E |  | Suitable Dimensions
|  |  | 2000 |  |  |  | +: 6; +: 500; ): 60 |  |  |  | Suitable Dimensions
|  |  | - | [14 empty] | - | bar: +; +; )
ABB
HITACHI | [6 empty] | *: CT / VT; ): Contract No. |  |  | N-19957.1-DF5W
[7 empty] | *: ADEQUACY CHECK; ): Date |  |  | 46106
0 | [6 empty] | *: LT14 - LEWIS 400/132kV SUBSTATION; ): Document No. |  |  | -
[7 empty] | ): Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | *: 33kV Side Trafo Feeder (100MVA); ): Contractor |  |  | HITACHI
| CT1L1 |  | Core3 |  | LV side |  | *: (Transformer Differential) |  |  |  | Connected devices: | SEL487E
CT1L2
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 5000 |  | 4000 |  | 3000 |  | / | 1 | A
Class of Accuracy: | bar: * to (
| CT Resistance: |  |  |  |  | Rct< | *: 20; Rct: W
| Knee Point Voltage: |  |  |  |  | Vk> | *: 1000; Rct: V | [7 empty] | Highest Vk required = |  |  | 58.3381
| Magnetizing Current: |  |  |  |  | I0< | *: 20; Rct: mA at Vk
Other Burdens on same CT core:
| Burden of |  | SEL487E |  |  |  | *: Sr'; (: =; Rct: 0.1; Rl: VA
| Burden of |  | 0 | bar: ( to Rl
| Burden of |  | 0 | bar: ( to Rl
| Total lead burden | [5 empty] | *: Sl'; (: =; Rct: 0.74045; Rl: VA
| Total lead + other burden | [5 empty] | *: Sl; (: =; Rct: 0.74045; Rl: VA
| Resisitance of the relay: | [5 empty] | +: Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 0.74045 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 0.74045 |  | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 132 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 132 | ) | bar: Resisitance of the relay: )
[9 empty] | 437.3866 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (LV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 437.3866 |  | x | 16
[12 empty] | Itf | = | 6998.1851 |  | A
ABB
Minimum required Knee point voltage (As per SEL guideline - Aug-2010)
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
| CT Primary Current | [13 empty] | Ipn |  | = | 5000 |  | A
| CT Internal Resistance | [13 empty] | Rct |  | = | 20 |  | W
| Burden of CT Leads | [13 empty] | Rl |  | = | 0.74045 |  | W
| Burden of the relay | [13 empty] | Rr |  | = | 0.1 |  | W
| Maximum through Fault Current on CT sec. | [13 empty] | If |  | = | 1.3996 |  | A
| Relay normal current | [13 empty] | Inrelay (Ir) |  | = | 1 |  | A
Minimum required Knee point voltage, hence,
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
|  | ³ | 2 | * | 1.3996 |  | * | ( | 20 | + | 0.74045 | + | 0.1 | )
|  | = | 58.3381 |  | V
|  |  | Available Vk |  |  | > | *: Required Vk
|  |  |  | 1000 |  | > | *: 58.3381
[5 empty] | Hence CT is: |  | *: Suitably Dimentioned
ABB
| CT1L1 |  | Core3 |  | LV side |  | *: (Transformer Differential) |  |  |  | Connected devices: | SEL487E
| CT1L2 | [17 empty] | 0
[7 empty] | *: Tap-1; Rct: Tap-2; Rl: Tap-3 |  |  |  |  | 0
| CT Ratio: | [5 empty] | 5000 |  | 4000 |  | 3000 |  | / | 1 | A
Class of Accuracy: | bar: Rct
| CT Resistance: | [5 empty] | (: Rct<; Rct: 15; Rl: W
| Knee Point Voltage: | [5 empty] | (: Vk>; Rct: 800; Rl: V | [7 empty] | Highest Vk required = |  |  | 55.4272
| Magnetizing Current: | [5 empty] | (: I0<; Rct: 40; Rl: mA at Vk
Other Burdens on same CT core:
| Burden of |  | SEL487E |  |  |  | *: Sr'; (: =; Rct: 0.1; Rl: VA
| Burden of |  | 0 |  |  |  | (: =; Rct: 0; Rl: VA
| Burden of |  | 0 |  |  |  | (: =; Rct: 0; Rl: VA
| Total lead burden | [5 empty] | *: Sl'; (: =; Rct: 0.74045; Rl: VA
| Total lead + other burden | [5 empty] | *: Sl; (: =; Rct: 0.74045; Rl: VA
| Resisitance of the relay: | [5 empty] | +: Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 0.74045 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 0.74045 |  | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 132 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 132 | ) | bar: Resisitance of the relay: )
[9 empty] | 437.3866 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (LV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 437.3866 |  | x | 16
[12 empty] | Itf | = | 6998.1851 |  | A
ABB
Minimum required Knee point voltage (As per SEL guideline - Aug-2010)
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
| CT Primary Current | [13 empty] | Ipn |  | = | 4000 |  | A
| CT Internal Resistance | [13 empty] | Rct |  | = | 15 |  | W
| Burden of CT Leads | [13 empty] | Rl |  | = | 0.74045 |  | W
| Burden of the relay | [13 empty] | Rr |  | = | 0.1 |  | W
| Maximum through Fault Current on CT sec. | [13 empty] | If |  | = | 1.7495 |  | A
| Relay normal current | [13 empty] | Inrelay (Ir) |  | = | 1 |  | A
Minimum required Knee point voltage, hence,
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
|  | ³ | 2 | * | 1.7495 |  | * | ( | 15 | + | 0.74045 | + | 0.1 | )
|  | = | 55.4272 |  | V
|  |  | Available Vk |  |  | > | *: Required Vk
|  |  |  | 800 |  | > | *: 55.4272
[5 empty] | Hence CT is: |  | *: Suitably Dimentioned
ABB
| CT1L1 |  | Core3 |  | LV side |  | *: (Transformer Differential) |  |  |  | Connected devices: | SEL487E
| CT1L2 | [17 empty] | 0
[7 empty] | *: Tap-1; Rct: Tap-2; Rl: Tap-3 |  |  |  |  | 0
| CT Ratio: | [5 empty] | 5000 |  | 4000 |  | 3000 |  | / | 1 | A
Class of Accuracy: | bar: Rl
| CT Resistance: | [5 empty] | +: Rct<; Rl: 10; Rr: W
| Knee Point Voltage: | [5 empty] | +: Vk>; Rl: 800; Rr: V | [7 empty] | Highest Vk required = |  |  | 50.5757
| Magnetizing Current: | [5 empty] | +: I0<; Rl: 50; Rr: mA at Vk
Other Burdens on same CT core:
| Burden of |  | SEL487E |  |  |  | *: Sr'; (: =; Rct: 0.1; Rl: VA
| Burden of |  | 0 |  |  |  | (: =; Rct: 0; Rl: VA
| Burden of |  | 0 |  |  |  | (: =; Rct: 0; Rl: VA
| Total lead burden | [5 empty] | *: Sl'; (: =; Rct: 0.74045; Rl: VA
| Total lead + other burden | [5 empty] | *: Sl; (: =; Rct: 0.74045; Rl: VA
| Resisitance of the relay: | [5 empty] | +: Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 0.74045 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 0.74045 |  | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 132 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 132 | ) | bar: Resisitance of the relay: )
[9 empty] | 437.3866 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (LV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 437.3866 |  | x | 16
[12 empty] | Itf | = | 6998.1851 |  | A
ABB
Minimum required Knee point voltage (As per SEL guideline - Aug-2010)
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
| CT Primary Current | [13 empty] | Ipn |  | = | 3000 |  | A
| CT Internal Resistance | [13 empty] | Rct |  | = | 10 |  | W
| Burden of CT Leads | [13 empty] | Rl |  | = | 0.74045 |  | W
| Burden of the relay | [13 empty] | Rr |  | = | 0.1 |  | W
| Maximum through Fault Current on CT sec. | [13 empty] | If |  | = | 2.3327 |  | A
| Relay normal current | [13 empty] | Inrelay (Ir) |  | = | 1 |  | A
Minimum required Knee point voltage, hence,
| Vk | ³ | 2 | * | If |  | * | ( | Rct | + | Rl | + | Rr | ) | [5 empty] | ---(1)
|  | ³ | 2 | * | 2.3327 |  | * | ( | 10 | + | 0.74045 | + | 0.1 | )
|  | = | 50.5757 |  | V
|  |  | Available Vk |  |  | > | *: Required Vk
|  |  |  | Sr' |  | > | *: 50.5757
[5 empty] | Hence CT is: |  | *: Suitably Dimentioned
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  |  |  | CT Cable m/mm2 |  | Class |  | CT Resistance (W) @ 75OC |  | CT Resistance (W) @ 75OC | Knee point Voltage (Vk), V |  |  | Mag. Current (Io), mA at Vk |  |  | Relay / Instrument Type
CT1L1 | CT1L2 | Core3 | 5000 | 4000 | 3000 | 1 | 120 | 6 | PX |  | 20 | 15 | 10 | 1000 | 800 | 800 | 20 | 40 | 50 | SEL487E
CT1L2 | 0
0 | CT Ratio:
ABB

## BCU+OC-5P SEL751+7SJ85 (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV Side Trafo Feeder (100MVA) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core3 |  |  |  | (OC +BCU) | [10 empty] | Connected devices: | 7SJ85
SEL751
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | FMS
| CT Ratio: | [5 empty] | 3150 |  | 2000 |  | - |  | / | 1 | A |  |  |  | AVR
| Class of Accuracy: | [5 empty] | 5P | 20
| CT Resistance: |  |  |  |  | Rct< | 9 |  | W
| Rated Burden |  |  |  |  | PN | 7.5 |  | VA | [12 empty] | Suitably Dimensioned
Other Burdens on same CT core:
| Burden of |  | 7SJ85 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | SEL751 |  |  |  |  | = | 0.02 |  | VA
| Burden of |  | FMS |  |  |  |  | = | 0.058 |  | VA
| Burden of |  | AVR | [5 empty] | 0.2 |  | VA |  | PE | = | In | x | In | x | Rct
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1 | x | 1 | x | 9
| Total lead + other burden | [5 empty] | PL | = | 1.375 |  | VA |  |  | = | 9 |  | VA
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 31500 |  | A | ** |  | This Current Must be Linked Later to Fault Setting
|  | CT Primary Current, | [13 empty] | Ipn | = | 3150 |  | A
|  | Internal Burden, | [13 empty] | PE | = | 9 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.375 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN | = | 7.5 |  | VA
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 31500 |  | / | 3150
[5 empty] | = | 10
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 9 | + | 7.5 | ) / ( | 9 | + | 1.375 | )
[5 empty] | = | 31.8072
|  |  |  | Available Kssc' | = =: >; 10 n: Required Kssc'
|  |  | 31.8072 |  | = =: >; 10 n: 10
|  |  |  | Hence CT is: | 10 n: Suitably Dimensioned
** Assumed
| T1 |  | Core3 |  | 10 x ( (: (OC +BCU) |  |  | Connected devices: | 7SJ85
| 0 | [17 empty] | SEL751
[5 empty] | 10 x ( (: Tap-1; 10 +: Tap-2; 10 ) / (: Tap-3 |  |  |  | FMS
| CT Ratio: |  |  |  | 10 x ( (: 3150; 10 +: 2000; 10 ) / (: -; 10 +: /; 10 PL: 1; 10 ): A |  |  |  | AVR
| Class of Accuracy: |  |  |  | 10 +: 5P; 10 PN: 20
| CT Resistance: |  |  |  | 10 PE: Rct<; 10 +: 5; 10 ) / (: W
| Rated Burden |  |  |  | 10 PE: PN; 10 +: 5; 10 ) / (: VA | [6 empty] | Suitably Dimentioned
Other Burdens on same CT core:
| Burden of |  | 7SJ85 |  | 10 PE: =; 10 +: 0.02; 10 ) / (: VA; 10 +: CT internal Burden
| Burden of |  | SEL751 |  | 10 PE: =; 10 +: 0.02; 10 ) / (: VA
| Burden of |  | FMS |  | 10 PE: =; 10 +: 0.058; 10 ) / (: VA
| Burden of |  | AVR |  | 10 +: 0.2; 10 ) / (: VA; 10 +: PE; 10 PL: =; 10 ): In | x | In | x | Rct
| Total lead burden |  |  |  | 10 PE: =; 10 +: 1.077; 10 ) / (: VA; 10 PL: =; 10 ): 1 | x | 1 | x | 5
| Total lead + other burden |  |  |  | 10 x ( (: PL; 10 PE: =; 10 +: 1.375; 10 ) / (: VA; 10 PL: =; 10 ): 5 |  | VA
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 31500 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2000 |  | A
|  | Internal Burden, | [13 empty] | PE | = | 5 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.375 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN | = | 5 |  | VA
|  |  |  | Required Kssc' | = =: =; 10 n: Itkmax; 10 PE: /; 10 +: Ipn
[5 empty] | = | 31500 |  | / | 2000
[5 empty] | = | 15.75
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 5 | + | 5 | ) / ( | 5 | + | 1.375 | )
[5 empty] | = | 31.3724
|  |  |  | Available Kssc' | = =: >; 15.75 n: Required Kssc'
|  |  | 31.3724 |  | = =: >; 15.75 n: 15.75
|  |  |  | Hence CT is: | 15.75 n: Suitably Dimentioned
| T1 |  | Core3 |  | 15.75 x ( (: (OC +BCU) |  |  | Connected devices: | 7SJ85
| 0 | [17 empty] | SEL751
[5 empty] | 15.75 x ( (: Tap-1; 15.75 +: Tap-2; 15.75 ) / (: Tap-3 |  |  |  | FMS
| CT Ratio: |  |  |  | 15.75 x ( (: 3150; 15.75 +: 2000; 15.75 ) / (: -; 15.75 +: /; 15.75 PL: 1; 15.75 ): A
| Class of Accuracy: |  |  |  | 15.75 ) / (: 5P; 15.75 PE: 20
| CT Resistance: |  |  |  | 15.75 PN: Rct<; 15.75 ) / (: -; 15.75 +: W
| Rated Burden |  |  |  | 15.75 PN: PN; 15.75 ) / (: -; 15.75 +: VA | [6 empty] | #VALUE!
Other Burdens on same CT core:
| Burden of |  | 7SJ85 |  | 15.75 PE: =; 15.75 +: 0.02; 15.75 ) / (: VA; 15.75 +: CT internal Burden
| Burden of |  | SEL751 |  | 15.75 PE: =; 15.75 +: 0.02; 15.75 ) / (: VA
| Burden of |  | FMS |  | 15.75 PE: =; 15.75 +: 0.058; 15.75 ) / (: VA; 15.75 +: PE; 15.75 PL: =; 15.75 ): In | x | In | x | Rct
| Total lead burden |  |  |  | 15.75 PE: =; 15.75 +: 1.077; 15.75 ) / (: VA; 15.75 PL: =; 15.75 ): 1 | x | 1 | x | -
| Total lead + other burden |  |  |  | 15.75 x ( (: PL; 15.75 PE: =; 15.75 +: 1.175; 15.75 ) / (: VA; 15.75 PL: =; 15.75 ): #VALUE! |  | VA
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 31500 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2000 |  | A
|  | Internal Burden, | [13 empty] | PE | = | #VALUE! |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN | = | - |  | VA
|  |  |  | Required Kssc' | = =: =; 15.75 n: Itkmax; 15.75 PE: /; 15.75 +: Ipn
[5 empty] | = | 31500 |  | / | 2000
[5 empty] | = | 15.75
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 1.175 | )
[5 empty] | = | #VALUE!
|  |  |  | Available Kssc' | = =: #VALUE!; 15.75 n: Required Kssc'
|  |  | #VALUE! |  | = =: #VALUE!; 15.75 n: 15.75
|  |  |  | Hence CT is: | 15.75 n: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | 15.75 n: CT Cable m/mm2; 15.75 PE: Class; 15.75 PN: CT Resistance (W) @ 75OC; 15.75 PE: Rated Burden of CT, VA | Relay / Instrument Type |  | CT Suitability
T1 | Core3 |  | 3150 |  | 1 | 120 | 6 | 5P | 20 | 9 |  | 7.5 |  | - |  | 7SJ85 SEL751 FMS AVR |  | Suitably Dimensioned
|  |  | 2000 |  | 15.75 PN: 5; 15.75 PE: 5; 15.75 PL: - |  |  | Suitably Dimentioned
|  |  | - | [14 empty] | - | bar: 15.75 PN; 15.75 PE; 15.75 PL

## Tariff Main-0.2FS (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | 33kV Side Trafo Feeder (100MVA) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core4 |  |  | (Tariff Meter- Main) | [10 empty] | Connected devices: | XC-RACK
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 3150 |  | 2000 |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.2sFS5
| CT Resistance: |  |  |  | Rct< | 9 |  | W
| Factor of Safety |  |  |  | FS | 5 | [13 empty] | Suitable Dimensions
| Rated Burden |  |  |  | PN | 10 |  | VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [8 empty] | rec670 | 100A for 1 S
| Burden of |  | 0 |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 9
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 9 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 1.085 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 3150 |  | A
| Internal Burden, | [10 empty] | PE | = | 9 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 1.085 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | n | = | 10
| Safety Factor among all connected devices Fs (min) | [11 empty] | = | 20 |  | ** | Assumed
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 1.085
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 5 | x ( ( | 9 | + | 10 | ) / ( | 9 | + | 1.085 | )
[7 empty] | = | 9.4199
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.085 FS: Total Connected Burden; 1.085 ): …cond.1
[5 empty] | 10 |  | = =: >; 1.085 FS: 1.085; 1.085 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.085 FS: Effective Safety Factor of CT, FS'; 1.085 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.085 FS: 9.4199; 1.085 ): Satisfied
[6 empty] | Hence CT is: | 1.085 FS: Suitable Dimensions
| T1 |  | Core4 |  |  | (Tariff Meter- Main) | 1.085 ): Connected devices: | XC-RACK
0
[6 empty] | Tap-1 | 1.085 FS: Tap-2; 1.085 PE: Tap-3
| CT Ratio: |  |  |  |  | 3150 | 1.085 FS: 2000; 1.085 PE: -; 1.085 PN: /; 1.085 ) / (: 1; 1.085 PE: A
| Class of Accuracy: | [5 empty] | 1.085 FS: 0.2sFS5
| CT Resistance: | [5 empty] | = =: Rct<; 1.085 FS: 5; 1.085 PE: W
| Factor of Safety | [5 empty] | = =: FS; 1.085 FS: 5 |  |  | Suitable Dimensions
| Rated Burden | [5 empty] | = =: PN; 1.085 FS: 7.5; 1.085 PE: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 1.085 FS: 0.008; 1.085 PE: VA; 1.085 PN: CT internal Burden
| Burden of |  | 0 |  |  |  | = =: =; 1.085 FS: 0; 1.085 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = =: =; 1.085 FS: 1.077; 1.085 PE: VA; 1.085 ) / (: =; 1.085 PE: 5; 1.085 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.085 FS: 1.085; 1.085 PE: VA
| CT Primary Current, | [5 empty] | 1.085 PN: Ipn; 1.085 ) / (: =; 1.085 PE: 2000; 1.085 PL: A
| Internal Burden, | [5 empty] | 1.085 PN: PE; 1.085 ) / (: =; 1.085 PE: 5; 1.085 PL: VA
| Burden of CT Leads and burden of connected devices | [5 empty] | 1.085 PN: PL; 1.085 ) / (: =; 1.085 PE: 1.085; 1.085 PL: VA
| Rated Secondary Current, | [5 empty] | 1.085 PN: In; 1.085 ) / (: =; 1.085 PE: 1; 1.085 PL: A
| CT Safety Factor | [5 empty] | 1.085 PN: n; 1.085 ) / (: =; 1.085 PE: 10
| Safety Factor among all connected devices Fs (min) | [5 empty] | 1.085 ) / (: =; 1.085 PE: 20; 1.085 PL: **; 1.085 ): Assumed
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.085 +: Fs(min); 1.085 PL: =; 1.085 ): 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.085 FS: Connected devices burden; 1.085 PE: +; 1.085 +: Lead Burden
[7 empty] | = | 1.085
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 5 | x ( ( | 5 | + | 7.5 | ) / ( | 5 | + | 1.085 | )
[7 empty] | = | 10.2711
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.085 FS: Total Connected Burden; 1.085 ): …cond.1
[5 empty] | 7.5 |  | = =: >; 1.085 FS: 1.085; 1.085 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.085 FS: Effective Safety Factor of CT, FS'; 1.085 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.085 FS: 10.2711; 1.085 ): Satisfied
[6 empty] | Hence CT is: | 1.085 FS: Suitable Dimensions
| T1 |  | Core4 |  |  | (Tariff Meter- Main)
0
[6 empty] | Tap-1 | 1.085 FS: Tap-2; 1.085 PE: Tap-3
| CT Ratio: |  |  |  |  | 3150 | 1.085 FS: 2000; 1.085 PE: -; 1.085 PN: /; 1.085 ) / (: 1; 1.085 PE: A
| Class of Accuracy: | [5 empty] | 1.085 PE: 0.2sFS5
| CT Resistance: | [5 empty] | 1.085 x ( (: Rct<; 1.085 PE: -; 1.085 PN: W
| Factor of Safety | [18 empty] | #VALUE! | bar: 1.085 x ( ( to 1.085 +
| Rated Burden | [5 empty] | 1.085 x ( (: PN; 1.085 PE: -; 1.085 PN: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 1.085 FS: 0.008; 1.085 PE: VA; 1.085 PN: CT internal Burden
| Burden of |  | 0 |  |  |  | = =: =; 1.085 FS: 0; 1.085 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [5 empty] | = =: =; 1.085 FS: 1.077; 1.085 PE: VA; 1.085 ) / (: =; 1.085 PE: #VALUE!; 1.085 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.085 FS: 1.085; 1.085 PE: VA
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.085 +: Fs(min); 1.085 PL: =; 1.085 ): 20
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.085 FS: CT Int. Burden; 1.085 +: +; 1.085 PN: Connected Burden
[7 empty] | = | #VALUE! |  | + | 1.085
[7 empty] | = | #VALUE!
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | - | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 1.085 | )
[7 empty] | = | #VALUE!
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; #VALUE! FS: Total Connected Burden; #VALUE! ): …cond.1
[5 empty] | - |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; #VALUE! FS: Effective Safety Factor of CT, FS'; #VALUE! ): …cond.2
[5 empty] | 20 |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
[6 empty] | Hence CT is: | #VALUE! FS: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; #VALUE! x ( (: CT Resistance (W) @ 75OC; #VALUE! +: Rated Burden VA; #VALUE! +: Relay / Instrument Type; #VALUE! ): CT Suitability
T1 | Core4 |  | 3150 | 1 | 120 | 6 | = =: 0.2sFS5; #VALUE! x ( (: 9; #VALUE! +: 10; #VALUE! ) / (: -; #VALUE! +: XC-RACK; #VALUE! ): Suitable Dimensions
|  |  | 2000 |  |  |  | #VALUE! x ( (: 5; #VALUE! +: 7.5; #VALUE! ) / (: -; #VALUE! ): Suitable Dimensions
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )

## Tariff Check-0.2FS (2) (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | 33kV Side Trafo Feeder (100MVA) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core5 |  |  | (Tariff Meter- Check) | [10 empty] | Connected devices: | XC-RACK
GOSSEN
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 3150 |  | 2000 |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.2sFS5
| CT Resistance: |  |  |  | Rct< | 9 |  | W
| Factor of Safety |  |  |  | FS | 5 | [13 empty] | Suitable Dimensions
| Rated Burden |  |  |  | PN | 10 |  | VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [8 empty] | rec670 | 100A for 1 S
| Burden of |  | GOSSEN |  |  |  | = | 0.25 |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 9
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 9 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 1.335 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 3150 |  | A
| Internal Burden, | [10 empty] | PE | = | 9 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 1.335 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | n | = | 10
| Safety Factor among all connected devices Fs (min) | [11 empty] | = | 20 |  | ** | Assumed
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 1.335
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 5 | x ( ( | 9 | + | 10 | ) / ( | 9 | + | 1.335 | )
[7 empty] | = | 9.192
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.335 FS: Total Connected Burden; 1.335 ): …cond.1
[5 empty] | 10 |  | = =: >; 1.335 FS: 1.335; 1.335 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.335 FS: Effective Safety Factor of CT, FS'; 1.335 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.335 FS: 9.192; 1.335 ): Satisfied
[6 empty] | Hence CT is: | 1.335 FS: Suitable Dimensions
| T1 |  | Core5 |  |  | (Tariff Meter- Check) | 1.335 ): Connected devices: | XC-RACK
| 0 | [16 empty] | GOSSEN
[6 empty] | Tap-1 | 1.335 FS: Tap-2; 1.335 PE: Tap-3
| CT Ratio: |  |  |  |  | 3150 | 1.335 FS: 2000; 1.335 PE: -; 1.335 PN: /; 1.335 ) / (: 1; 1.335 PE: A
| Class of Accuracy: | [5 empty] | 1.335 FS: 0.2sFS5
| CT Resistance: | [5 empty] | = =: Rct<; 1.335 FS: 5; 1.335 PE: W
| Factor of Safety | [5 empty] | = =: FS; 1.335 FS: 5 |  |  | Suitable Dimensions
| Rated Burden | [5 empty] | = =: PN; 1.335 FS: 7.5; 1.335 PE: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 1.335 FS: 0.008; 1.335 PE: VA; 1.335 PN: CT internal Burden
| Burden of |  | GOSSEN |  |  |  | = =: =; 1.335 FS: 0.25; 1.335 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = =: =; 1.335 FS: 1.077; 1.335 PE: VA; 1.335 ) / (: =; 1.335 PE: 5; 1.335 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.335 FS: 1.335; 1.335 PE: VA
| CT Primary Current, | [5 empty] | 1.335 PN: Ipn; 1.335 ) / (: =; 1.335 PE: 2000; 1.335 PL: A
| Internal Burden, | [5 empty] | 1.335 PN: PE; 1.335 ) / (: =; 1.335 PE: 5; 1.335 PL: VA
| Burden of CT Leads and burden of connected devices | [5 empty] | 1.335 PN: PL; 1.335 ) / (: =; 1.335 PE: 1.335; 1.335 PL: VA
| Rated Secondary Current, | [5 empty] | 1.335 PN: In; 1.335 ) / (: =; 1.335 PE: 1; 1.335 PL: A
| CT Safety Factor | [5 empty] | 1.335 PN: n; 1.335 ) / (: =; 1.335 PE: 10
| Safety Factor among all connected devices Fs (min) | [5 empty] | 1.335 ) / (: =; 1.335 PE: 20; 1.335 PL: **; 1.335 ): Assumed
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.335 +: Fs(min); 1.335 PL: =; 1.335 ): 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.335 FS: Connected devices burden; 1.335 PE: +; 1.335 +: Lead Burden
[7 empty] | = | 1.335
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 5 | x ( ( | 5 | + | 7.5 | ) / ( | 5 | + | 1.335 | )
[7 empty] | = | 9.8658
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.335 FS: Total Connected Burden; 1.335 ): …cond.1
[5 empty] | 7.5 |  | = =: >; 1.335 FS: 1.335; 1.335 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.335 FS: Effective Safety Factor of CT, FS'; 1.335 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.335 FS: 9.8658; 1.335 ): Satisfied
[6 empty] | Hence CT is: | 1.335 FS: Suitable Dimensions
| T1 |  | Core5 |  |  | (Tariff Meter- Check)
0
[6 empty] | Tap-1 | 1.335 FS: Tap-2; 1.335 PE: Tap-3
| CT Ratio: |  |  |  |  | 3150 | 1.335 FS: 2000; 1.335 PE: -; 1.335 PN: /; 1.335 ) / (: 1; 1.335 PE: A
| Class of Accuracy: | [5 empty] | 1.335 PE: 0.2sFS5
| CT Resistance: | [5 empty] | 1.335 x ( (: Rct<; 1.335 PE: -; 1.335 PN: W
| Factor of Safety | [18 empty] | #VALUE! | bar: 1.335 x ( ( to 1.335 +
| Rated Burden | [5 empty] | 1.335 x ( (: PN; 1.335 PE: -; 1.335 PN: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 1.335 FS: 0.008; 1.335 PE: VA; 1.335 PN: CT internal Burden
| Burden of |  | GOSSEN |  |  |  | = =: =; 1.335 FS: 0.25; 1.335 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [5 empty] | = =: =; 1.335 FS: 1.077; 1.335 PE: VA; 1.335 ) / (: =; 1.335 PE: #VALUE!; 1.335 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.335 FS: 1.335; 1.335 PE: VA
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.335 +: Fs(min); 1.335 PL: =; 1.335 ): 20
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.335 FS: CT Int. Burden; 1.335 +: +; 1.335 PN: Connected Burden
[7 empty] | = | #VALUE! |  | + | 1.335
[7 empty] | = | #VALUE!
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | - | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 1.335 | )
[7 empty] | = | #VALUE!
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; #VALUE! FS: Total Connected Burden; #VALUE! ): …cond.1
[5 empty] | - |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; #VALUE! FS: Effective Safety Factor of CT, FS'; #VALUE! ): …cond.2
[5 empty] | 20 |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
[6 empty] | Hence CT is: | #VALUE! FS: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; #VALUE! x ( (: CT Resistance (W) @ 75OC; #VALUE! +: Rated Burden VA; #VALUE! +: Relay / Instrument Type; #VALUE! ): CT Suitability
T1 | Core5 |  | 3150 | 1 | 120 | 6 | = =: 0.2sFS5; #VALUE! x ( (: 9; #VALUE! +: 10; #VALUE! ) / (: -; #VALUE! +: XC-RACK GOSSEN; #VALUE! ): Suitable Dimensions
|  |  | 2000 |  |  |  | #VALUE! x ( (: 5; #VALUE! +: 7.5; #VALUE! ) / (: -; #VALUE! ): Suitable Dimensions
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )

## 7UT635-X (hidden)
[7 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-16682
[7 empty] | CALCULATION | [6 empty] | Date |  |  | 45276
HITACHI ENERGY - GRID AUTOMATION | [6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | N16682-CB-0070-J-7901
[14 empty] | Revision No. |  |  | A
Prep. By |  | PK | Checked By |  |  | RN | 33kV Incomer Transformer Feeder | [6 empty] | Contractor |  |  | HITACHI ENERGY
| T1 |  | Core2 |  |  |  | (Transformer Differential) | [10 empty] | Connected devices: | 7UT85
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX
| CT Resistance: |  |  |  |  | Rct< | 10 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 400 |  | V | [12 empty] | Highest Vk required = |  |  |  |  | 89.42
| Magnetizing Current: |  |  |  |  | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | 7UT85 |  |  |  | Sr' | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Total lead burden | [5 empty] | Sl' | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | Sl | = | 1.077 |  | VA
| Resisitance of the relay: | [10 empty] | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 1.077 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, Rb' |  |  | = | 0.1 |  | + | 1.077 |  | = | 1.177 |  | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 33 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 33 | ) | bar: Resisitance of the relay: )
[9 empty] | 1749.5463 |  | A | bar: Resisitance of the relay: )
The internal fault current shall be 50kA.
Internal Fault Current (LV Side) | [12 empty] | = | 50000 |  | A
| Vk | ³ |  |  |  | 0.4 | x | Isccmax (int. fault) |  |  |  |  | x ( | Rct | + | Rbc | ) x | Isr |  | ---(1)
Ipr
| Resisitance of the relay: Rr: Rated primary current of the current transformer | [6 empty] | Ipr |  | = | 2500 |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [6 empty] | Rct |  | = | 10 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [6 empty] | Rbc |  | = | 1.177 |  | W
| Resisitance of the relay: Rr: Rated secondary current of the current transformer | [6 empty] | Isn |  | = | 1 |  | A
| Resisitance of the relay: Rr: Max fault current at close-in fault | [6 empty] | Isccmax (int. fault) |  | = | 50000 |  | A
| Resisitance of the relay: Rr: Transformer nominal current | [6 empty] | Ino |  | = | 1749.5463 |  | A
| Resisitance of the relay: Rr: Relay normal current | [6 empty] | Inrelay (Ir) |  | = | 1 |  | A
| Vk | ³ |  |  |  | 0.4 | x | 50000 |  |  |  |  | x ( | 10 | + | 1.177 | ) x | 1 |  | ---(1)
2500
|  | = | 89.42 |  | V
Maximum through Fault Current (LV Side) | [11 empty] | Itf | = | Int |  | / | Percentage Impedance
[13 empty] | = | 1749.5463 |  | / | 0.25
[12 empty] | Itf | = | 6998.1851 |  | A
| Vk | ³ |  |  |  | 1.6 | x | Isccmax (Ext. fault) |  |  |  |  | x ( | Rct | + | Rbc | ) x | Isr |  | ---(2)
Ipr
| Resisitance of the relay: Rr: Rated primary current of the current transformer | [6 empty] | Ipr |  | = | 2500 |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [6 empty] | Rct |  | = | 10 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [6 empty] | Rbc |  | = | 1.177 |  | W
| Resisitance of the relay: Rr: Rated secondary current of the current transformer | [6 empty] | Isn |  | = | 1 |  | A
| Resisitance of the relay: Rr: Max fault current at close-in fault | [6 empty] | Isccmax (Ext. fault) |  | = | 6998.1851 |  | A
| Resisitance of the relay: Rr: Transformer nominal current | [6 empty] | Ino |  | = | 1749.5463 |  | A
| Resisitance of the relay: Rr: Relay normal current | [6 empty] | Inrelay (Ir) |  | = | 1 |  | A
| Vk | ³ |  |  |  | 1.6 | x | 6998.1851 |  |  |  |  | x ( | 10 | + | 1.177 | ) x | 1 |  | ---(2)
2500
|  | = | 50.07 |  | V
At least | [19 empty] | ---(3)
|  |  |  | Vk | ³ | 20 | x | Isr | x ( | Rct | + | Rbc | )
| Resisitance of the relay: Rr: CT Internal Resistance | [6 empty] | Rct |  | = | 10 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [6 empty] | Rbc |  | = | 1.177 |  | W
| Resisitance of the relay: Rr: Rated secondary current of the current transformer | [6 empty] | Isr |  | = | 1 |  | A
|  |  |  | Vk | ³ | 20 | x | 1 | x ( | 10 | + | 1.177 | )
[5 empty] | = | 223.55
| Resisitance of the relay: Sr': KPV as per Hitachi recommendation |  |  | Vk | ≥ | max(89.42,50.07,223.55) | [9 empty] | ( | max | , | )
[11 empty] | Vk | ≥ | 223.55
[11 empty] | 400 | ≥ | 223.55
[5 empty] | Hence CT is: |  | Suitably Dimensioned
ABB
| Resisitance of the relay: Rr: T1; Resisitance of the relay: Sr': Core2; Resisitance of the relay: Ir: HV side; Resisitance of the relay: Ir: (Transformer Differential) | [9 empty] | Connected devices: | 7UT85
| Resisitance of the relay: Rr: 0 | [10 empty] | 0
| Resisitance of the relay: Ir: Tap-1 | Tap-2 |  | Tap-3 | [7 empty] | 0
| Resisitance of the relay: Rr: CT Ratio:; Resisitance of the relay: Ir: 2500 | - |  | - |  | / | 1 | A
| Resisitance of the relay: Rr: Class of Accuracy: | PX
| Resisitance of the relay: Rr: CT Resistance:; Resisitance of the relay: ): Rct< | 5 |  | W
| Resisitance of the relay: Rr: Knee Point Voltage:; Resisitance of the relay: ): Vk> | 300 |  | V | [10 empty] | Highest Vk required = |  |  |  |  | #VALUE!
| Resisitance of the relay: Rr: Magnetizing Current:; Resisitance of the relay: ): I0< | 40 |  | mA at Vk
Other Burdens on same CT core:
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 7UT85; Resisitance of the relay: Ir: Sr'; Resisitance of the relay: ): = | 0.1 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Total lead burden; Resisitance of the relay: Ir: Sl'; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Total lead + other burden; Resisitance of the relay: Ir: Sl; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Resisitance of the relay: |  |  |  | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 1.077 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, Rb' |  |  | = | 0.1 |  | + | 1.077 |  | = | 1.177 |  | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 33 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 33 | ) | bar: Resisitance of the relay: )
[9 empty] | 1749.5463 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (HV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 1749.5463 |  | x | 16
[12 empty] | Itf | = | 27992.7403 |  | A
ABB
Minimum required Knee point voltage (Siemens SIP - 2008, page 2/53)
| Vk | ³ |  |  |  | Ktd | x | Isccmax (ext. fault) |  |  |  |  | x ( | Rct | + | Rb' | ) x | Isn |  | ---(1)
| Resisitance of the relay: ): 1.3 |  | x | Ipn
| Resisitance of the relay: Rr: CT Primary Current | [6 empty] | Ipn |  | = | - |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [6 empty] | Rct |  | = | 5 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [6 empty] | R'b |  | = | 1.177 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [6 empty] | Isn |  | = | 1 |  | A
| Resisitance of the relay: Rr: Max fault current at close-in fault | [6 empty] | Isccmax (ext. fault) |  | = | 27992.7403 |  | A
| Resisitance of the relay: Rr: Transformer normal current | [6 empty] | Ino |  | = | 1749.5463 |  | A
| Resisitance of the relay: Rr: Relay normal current | [6 empty] | Inrelay (Ir) |  | = | 1 |  | A
Transient dimentioning factor, Ktd = | Resisitance of the relay: Ir: 3; Resisitance of the relay: ): for Transformer |  |  |  | Hence,
| Vk | ³ |  |  |  | 3 | x | 27992.7403 |  |  |  |  | x ( | 5 | + | 1.177 | ) x | 1 |  | ---(1)
| Resisitance of the relay: ): 1.3 |  | x | -
|  | = | #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | Required Vk
|  |  |  | 300 |  | #VALUE! | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
Adaption Factor (Fadap) check:
| Resisitance of the relay: Sr': Fadap; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Ipn; Resisitance of the relay: ): x | Inrelay
| Resisitance of the relay: x: Ino | Isn
| Resisitance of the relay: Ir: =; Resisitance of the relay: x: -; Resisitance of the relay: ): x | 1
| Resisitance of the relay: x: 1749.5463 | 1
[5 empty] | = | #VALUE!
| Resisitance of the relay: Sr': 1/4; Resisitance of the relay: / (: ≤; Resisitance of the relay: Ir: Fadap; Resisitance of the relay: ): ≤ | 4 |  |  | ...for phase CTs | (ref. 2/57 of attached 7UT635 literature)
| Resisitance of the relay: Sr': 0.25; Resisitance of the relay: / (: #VALUE!; Resisitance of the relay: Ir: #VALUE!; Resisitance of the relay: ): #VALUE! | 4
| Adaption Factor (Fadap) = | [5 empty] | #VALUE!
ABB
| Resisitance of the relay: Rr: T1; Resisitance of the relay: Sr': Core2; Resisitance of the relay: Ir: HV side; Resisitance of the relay: Ir: (Transformer Differential) | [9 empty] | Connected devices: | 7UT85
| Resisitance of the relay: Rr: 0 | [10 empty] | 0
| Resisitance of the relay: Ir: Tap-1 | Tap-2 |  | Tap-3 | [7 empty] | 0
| Resisitance of the relay: Rr: CT Ratio:; Resisitance of the relay: Ir: 2500 | - |  | - |  | / | 1 | A
| Resisitance of the relay: Rr: Class of Accuracy: |  |  | PX
| Resisitance of the relay: Rr: CT Resistance: |  | Rct< | 3 |  | W
| Resisitance of the relay: Rr: Knee Point Voltage: |  | Vk> | 200 |  | V | [8 empty] | Highest Vk required = |  |  |  |  | #VALUE!
| Resisitance of the relay: Rr: Magnetizing Current: |  | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 7UT85; Resisitance of the relay: Ir: Sr'; Resisitance of the relay: ): = | 0.1 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Total lead burden; Resisitance of the relay: Ir: Sl'; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Total lead + other burden; Resisitance of the relay: Ir: Sl; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Resisitance of the relay: |  |  |  | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 1.077 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, Rb' |  |  | = | 0.1 |  | + | 1.077 |  | = | 1.177 |  | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 33 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 33 | ) | bar: Resisitance of the relay: )
[9 empty] | 1749.5463 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (HV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 1749.5463 |  | x | 16
[12 empty] | Itf | = | 27992.7403 |  | A
ABB
Minimum required Knee point voltage (Siemens SIP - 2008, page 2/53)
| Vk | ³ |  |  |  | Ktd | x | Isccmax (ext. fault) |  |  |  |  | x ( | Rct | + | Rb' | ) x | Isn |  | ---(1)
| Resisitance of the relay: ): 1.3 |  | x | Ipn
| Resisitance of the relay: Rr: CT Primary Current | [6 empty] | Ipn |  | = | - |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [6 empty] | Rct |  | = | 3 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [6 empty] | Rb' |  | = | 1.177 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [6 empty] | Isn |  | = | 1 |  | A
| Resisitance of the relay: Rr: Max fault current at close-in fault | [6 empty] | Isccmax (ext. fault) |  | = | 27992.7403 |  | A
| Resisitance of the relay: Rr: Transformer normal current | [6 empty] | Ino |  | = | 1749.5463 |  | A
| Resisitance of the relay: Rr: Relay normal current | [6 empty] | Inrelay (Ir) |  | = | 1 |  | A
Transient dimentioning factor, Ktd = | Resisitance of the relay: Ir: 3; Resisitance of the relay: ): for Transformer |  |  |  | Hence,
| Vk | ³ |  |  |  | 3 | x | 27992.7403 |  |  |  |  | x ( | 3 | + | 1.177 | ) x | 1 |  | ---(1)
| Resisitance of the relay: ): 1.3 |  | x | -
|  | = | #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | Required Vk
|  |  |  | 200 |  | #VALUE! | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
Adaption Factor (Fadap) check:
| Resisitance of the relay: Sr': Fadap; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Ipn; Resisitance of the relay: ): x | Inrelay
| Resisitance of the relay: x: Ino | Isn
| Resisitance of the relay: Ir: =; Resisitance of the relay: x: -; Resisitance of the relay: ): x | 1
| Resisitance of the relay: x: 1749.5463 | 1
[5 empty] | = | #VALUE!
| Resisitance of the relay: Sr': 1/4; Resisitance of the relay: / (: ≤; Resisitance of the relay: Ir: Fadap; Resisitance of the relay: ): ≤ | 4 |  |  | ...for phase CTs | (ref. 2/57 of attached 7UT635 literature)
| Resisitance of the relay: Sr': 0.25; Resisitance of the relay: / (: #VALUE!; Resisitance of the relay: Ir: #VALUE!; Resisitance of the relay: ): #VALUE! | 4
| Adaption Factor (Fadap) = | [5 empty] | #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core | Resisitance of the relay: Sr': Ratio (A); Resisitance of the relay: x: CT Cable m/mm2; Resisitance of the relay: ): Class |  | CT Resistance (W) @ 75OC |  | Limiting Secondary Voltage (Ual), V |  | Mag. Current (Io), mA at Vk |  | Relay / Instrument Type |  | CT Suitability
T1 | Core2 |  | 2500 |  | 1 | 120 | 6 | 0 |  | 10 |  | 400 |  | 50 |  | 7UT85 |  | Suitably Dimensioned
[10 empty] | - |  | - |  | - |  |  |  | - | bar: Resisitance of the relay: Sr'
[10 empty] | - |  | - |  | - |  |  |  | - | bar: Resisitance of the relay: Sr'
| Resisitance of the relay: Ir: CT / VT | [5 empty] | Contract No. |  |  | N-16682
| Resisitance of the relay: Ir: CALCULATION | [5 empty] | Date |  |  | 45276
HITACHI ENERGY - GRID AUTOMATION | Resisitance of the relay: Ir: LT14 - LEWIS 400/132kV SUBSTATION | [5 empty] | Document No. |  |  | N16682-CB-0070-J-7901
[14 empty] | Revision No. |  |  | A
Prep. By | Resisitance of the relay: =: PK; Resisitance of the relay: Sr': Checked By; Resisitance of the relay: x: RN; Resisitance of the relay: Ir: 33kV Incomer Transformer Feeder | [5 empty] | Contractor |  |  | HITACHI ENERGY
| Resisitance of the relay: Rr: CT1L1; Resisitance of the relay: Sr': Core3; Resisitance of the relay: Ir: LV side; Resisitance of the relay: Ir: (Transformer Differential) | [9 empty] | Connected devices: | 7UT85
CT1L2
| Resisitance of the relay: Ir: Tap-1 | Tap-2 |  | Tap-3
| Resisitance of the relay: Rr: CT Ratio:; Resisitance of the relay: Ir: 5000 | 4000 |  | 3000 |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX
| Resisitance of the relay: Rr: CT Resistance:; Resisitance of the relay: x: Rct<; Resisitance of the relay: Ir: 20 | W
| Resisitance of the relay: Rr: Knee Point Voltage:; Resisitance of the relay: x: Vk>; Resisitance of the relay: Ir: 1000 | V | [12 empty] | Highest Vk required = |  |  |  |  | 68.4003
| Resisitance of the relay: Rr: Magnetizing Current:; Resisitance of the relay: x: I0<; Resisitance of the relay: Ir: 20 | mA at Vk
Other Burdens on same CT core:
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 7UT85; Resisitance of the relay: Ir: Sr'; Resisitance of the relay: ): = | 0.1 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = |  |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = |  |  | VA
| Resisitance of the relay: Rr: Total lead burden; Resisitance of the relay: Ir: Sl'; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Total lead + other burden; Resisitance of the relay: Ir: Sl; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Resisitance of the relay: |  |  |  | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 1.077 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, Rb' |  |  | = | 0.1 | + | 1.077 | = | 1.177 | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 132 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 132 | ) | bar: Resisitance of the relay: )
[9 empty] | 437.3866 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (LV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 437.3866 |  | x | 16
[12 empty] | Itf | = | 6998.1851 |  | A
ABB
Minimum required Knee point voltage (Siemens SIP - 2008, page 2/53)
| Vk | ³ |  |  |  | Ktd | x | Isccmax (ext. fault) |  |  |  |  | x ( | Rct | + | Rb' | ) x | Isn |  | ---(1)
| Resisitance of the relay: ): 1.3 |  | x | Ipn
| Resisitance of the relay: Rr: CT Primary Current | [6 empty] | Ipn |  | = | 5000 |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [6 empty] | Rct |  | = | 20 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [6 empty] | R'b |  | = | 1.177 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [6 empty] | Isn |  | = | 1 |  | A
| Resisitance of the relay: Rr: Max fault current at close-in fault | [6 empty] | Isccmax (ext. fault) |  | = | 6998.1851 |  | A
| Resisitance of the relay: Rr: Transformer normal current | [6 empty] | Ino |  | = | 437.3866 |  | A
| Resisitance of the relay: Rr: Relay normal current | [6 empty] | Inrelay (Ir) |  | = | 1 |  | A
Transient dimentioning factor, Ktd = | Resisitance of the relay: Ir: 3; Resisitance of the relay: ): for Transformer |  |  |  | Hence,
| Vk | ³ |  |  |  | 3 | x | 6998.1851 |  |  |  |  | x ( | 20 | + | 1.177 | ) x | 1 |  | ---(1)
| Resisitance of the relay: ): 1.3 |  | x | 5000
|  | = | 68.4003 |  | V
|  |  | Available Vk |  |  | > | Required Vk
|  |  |  | 1000 |  | > | 68.4003
[5 empty] | Hence CT is: |  | Suitably Dimentioned
Adaption Factor (Fadap) check:
| Resisitance of the relay: Sr': Fadap; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Ipn; Resisitance of the relay: ): x | Inrelay
| Resisitance of the relay: x: Ino | Isn
| Resisitance of the relay: Ir: =; Resisitance of the relay: x: 5000; Resisitance of the relay: ): x | 1
| Resisitance of the relay: x: 437.3866 | 1
[5 empty] | = | 11.4315
| Resisitance of the relay: Sr': 1/4; Resisitance of the relay: / (: ≤; Resisitance of the relay: Ir: Fadap; Resisitance of the relay: ): ≤ | 4 |  |  | ...for phase CTs | (ref. 2/57 of attached 7UT635 literature)
| Resisitance of the relay: Sr': 0.25; Resisitance of the relay: / (: ≤; Resisitance of the relay: Ir: 11.4315; Resisitance of the relay: ): > | 4
| Adaption Factor (Fadap) = | [5 empty] | Not OK
ABB
| Resisitance of the relay: Rr: CT1L1; Resisitance of the relay: Sr': Core3; Resisitance of the relay: Ir: LV side; Resisitance of the relay: Ir: (Transformer Differential) | [9 empty] | Connected devices: | 7UT85
| Resisitance of the relay: Rr: CT1L2 | [10 empty] | 0
| Resisitance of the relay: Ir: Tap-1 | Tap-2 |  | Tap-3 | [7 empty] | 0
| Resisitance of the relay: Rr: CT Ratio:; Resisitance of the relay: Ir: 5000 | 4000 |  | 3000 |  | / | 1 | A
| Resisitance of the relay: Rr: Class of Accuracy: | PX
| Resisitance of the relay: Rr: CT Resistance:; Resisitance of the relay: ): Rct< | 15 |  | W
| Resisitance of the relay: Rr: Knee Point Voltage:; Resisitance of the relay: ): Vk> | 800 |  | V | [10 empty] | Highest Vk required = |  |  |  |  | 65.3133
| Resisitance of the relay: Rr: Magnetizing Current:; Resisitance of the relay: ): I0< | 40 |  | mA at Vk
Other Burdens on same CT core:
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 7UT85; Resisitance of the relay: Ir: Sr'; Resisitance of the relay: ): = | 0.1 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Total lead burden; Resisitance of the relay: Ir: Sl'; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Total lead + other burden; Resisitance of the relay: Ir: Sl; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Resisitance of the relay: |  |  |  | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 1.077 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, Rb' |  |  | = | 0.1 | + | 1.077 | = | 1.177 | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 132 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 132 | ) | bar: Resisitance of the relay: )
[9 empty] | 437.3866 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (LV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 437.3866 |  | x | 16
[12 empty] | Itf | = | 6998.1851 |  | A
ABB
Minimum required Knee point voltage (Siemens SIP - 2008, page 2/53)
| Vk | ³ |  |  |  | Ktd | x | Isccmax (ext. fault) |  |  |  |  | x ( | Rct | + | Rb' | ) x | Isn |  | ---(1)
| Resisitance of the relay: ): 1.3 |  | x | Ipn
| Resisitance of the relay: Rr: CT Primary Current | [6 empty] | Ipn |  | = | 4000 |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [6 empty] | Rct |  | = | 15 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [6 empty] | R'b |  | = | 1.177 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [6 empty] | Isn |  | = | 1 |  | A
| Resisitance of the relay: Rr: Max fault current at close-in fault | [6 empty] | Isccmax (ext. fault) |  | = | 6998.1851 |  | A
| Resisitance of the relay: Rr: Transformer normal current | [6 empty] | Ino |  | = | 437.3866 |  | A
| Resisitance of the relay: Rr: Relay normal current | [6 empty] | Inrelay (Ir) |  | = | 1 |  | A
Transient dimentioning factor, Ktd = | Resisitance of the relay: Ir: 3; Resisitance of the relay: ): for Transformer |  |  |  | Hence,
| Vk | ³ |  |  |  | 3 | x | 6998.1851 |  |  |  |  | x ( | 15 | + | 1.177 | ) x | 1 |  | ---(1)
| Resisitance of the relay: ): 1.3 |  | x | 4000
|  | = | 65.3133 |  | V
|  |  | Available Vk |  |  | > | Required Vk
|  |  |  | 800 |  | > | 65.3133
[5 empty] | Hence CT is: |  | Suitably Dimentioned
Adaption Factor (Fadap) check:
| Resisitance of the relay: Sr': Fadap; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Ipn; Resisitance of the relay: ): x | Inrelay
| Resisitance of the relay: x: Ino | Isn
| Resisitance of the relay: Ir: =; Resisitance of the relay: x: 4000; Resisitance of the relay: ): x | 1
| Resisitance of the relay: x: 437.3866 | 1
[5 empty] | = | 9.1452
| Resisitance of the relay: Sr': 1/4; Resisitance of the relay: / (: ≤; Resisitance of the relay: Ir: Fadap; Resisitance of the relay: ): ≤ | 4 |  |  | ...for phase CTs | (ref. 2/57 of attached 7UT635 literature)
| Resisitance of the relay: Sr': 0.25; Resisitance of the relay: / (: ≤; Resisitance of the relay: Ir: 9.1452; Resisitance of the relay: ): > | 4
| Adaption Factor (Fadap) = | [5 empty] | Not OK
ABB
| Resisitance of the relay: Rr: CT1L1; Resisitance of the relay: Sr': Core3; Resisitance of the relay: Ir: LV side; Resisitance of the relay: Ir: (Transformer Differential) | [9 empty] | Connected devices: | 7UT85
| Resisitance of the relay: Rr: CT1L2 | [10 empty] | 0
| Resisitance of the relay: Ir: Tap-1 | Tap-2 |  | Tap-3 | [7 empty] | 0
| Resisitance of the relay: Rr: CT Ratio:; Resisitance of the relay: Ir: 5000 | 4000 |  | 3000 |  | / | 1 | A
| Resisitance of the relay: Rr: Class of Accuracy: |  |  | PX
| Resisitance of the relay: Rr: CT Resistance: |  | Rct< | 10 |  | W
| Resisitance of the relay: Rr: Knee Point Voltage: |  | Vk> | 800 |  | V | [8 empty] | Highest Vk required = |  |  |  |  | 60.1684
| Resisitance of the relay: Rr: Magnetizing Current: |  | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 7UT85; Resisitance of the relay: Ir: Sr'; Resisitance of the relay: ): = | 0.1 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Total lead burden; Resisitance of the relay: Ir: Sl'; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Total lead + other burden; Resisitance of the relay: Ir: Sl; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Resisitance of the relay: |  |  |  | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.1 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.1; Resisitance of the relay: Ir: W |  |  |  |  | = | 1.077 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, Rb' |  |  | = | 0.1 | + | 1.077 | = | 1.177 | W
Power Transformer Data:
| Resisitance of the relay: Rr: Power Rating |  |  |  |  | = | 100 |  | MVA
| Resisitance of the relay: Rr: Percentage Impedance |  |  |  |  | = | 25 |  | %
| Resisitance of the relay: Rr: HV Rated Voltage, |  |  |  | Un1 | = | 132 |  | kV
Transformer Full load current | Resisitance of the relay: Ir: Int; Resisitance of the relay: ): = | MVA |  | x | 1000 | / | √3 | x | Un1 | )
[9 empty] | 100 |  | x | 1000 | / | √3 | x | 132 | ) | bar: Resisitance of the relay: )
[9 empty] | 437.3866 |  | A | bar: Resisitance of the relay: )
According to Clause 5.2 of ESI 48-3, the maximum through fault current shall be 16 times of the rated fault current.
Maximum through Fault Current (LV Side) | [11 empty] | Itf | = | Int |  | x | 16
[13 empty] | = | 437.3866 |  | x | 16
[12 empty] | Itf | = | 6998.1851 |  | A
ABB
Minimum required Knee point voltage (Siemens SIP - 2008, page 2/53)
| Vk | ³ |  |  |  | Ktd | x | Isccmax (ext. fault) |  |  |  |  | x ( | Rct | + | Rb' | ) x | Isn |  | ---(1)
| Resisitance of the relay: ): 1.3 |  | x | Ipn
| Resisitance of the relay: Rr: CT Primary Current | [6 empty] | Ipn |  | = | 3000 |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [6 empty] | Rct |  | = | 10 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [6 empty] | R'b |  | = | 1.177 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [6 empty] | Isn |  | = | 1 |  | A
| Resisitance of the relay: Rr: Max fault current at close-in fault | [6 empty] | Isccmax (ext. fault) |  | = | 6998.1851 |  | A
| Resisitance of the relay: Rr: Transformer normal current | [6 empty] | Ino |  | = | 437.3866 |  | A
| Resisitance of the relay: Rr: Relay normal current | [6 empty] | Inrelay (Ir) |  | = | 1 |  | A
Transient dimentioning factor, Ktd = | Resisitance of the relay: Ir: 3; Resisitance of the relay: ): for Transformer |  |  |  | Hence,
| Vk | ³ |  |  |  | 3 | x | 6998.1851 |  |  |  |  | x ( | 10 | + | 1.177 | ) x | 1 |  | ---(1)
| Resisitance of the relay: ): 1.3 |  | x | 3000
|  | = | 60.1684 |  | V
|  |  | Available Vk |  |  | > | Required Vk
|  |  |  | 800 |  | > | 60.1684
[5 empty] | Hence CT is: |  | Suitably Dimentioned
Adaption Factor (Fadap) check:
| Resisitance of the relay: Sr': Fadap; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Ipn; Resisitance of the relay: ): x | Inrelay
| Resisitance of the relay: x: Ino | Isn
| Resisitance of the relay: Ir: =; Resisitance of the relay: x: 3000; Resisitance of the relay: ): x | 1
| Resisitance of the relay: x: 437.3866 | 1
[5 empty] | = | 6.8589
| Resisitance of the relay: Sr': 1/4; Resisitance of the relay: / (: ≤; Resisitance of the relay: Ir: Fadap; Resisitance of the relay: ): ≤ | 4 |  |  | ...for phase CTs | (ref. 2/57 of attached 7UT635 literature)
| Resisitance of the relay: Sr': 0.25; Resisitance of the relay: / (: ≤; Resisitance of the relay: Ir: 6.8589; Resisitance of the relay: ): > | 4
| Adaption Factor (Fadap) = | [5 empty] | Not OK
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core | Resisitance of the relay: Sr': Ratio (A); Resisitance of the relay: Ir: CT Cable m/mm2 | Class |  | CT Resistance (W) @ 75OC |  | CT Resistance (W) @ 75OC | Knee point Voltage (Vk), V |  |  | Mag. Current (Io), mA at Vk |  |  | Relay / Instrument Type
CT1L1 | CT1L2 | Core3 | 5000 | 4000 | 3000 | 1 | 100 | 4 | PX |  | 20 | 15 | 10 | 1000 | 800 | 800 | 20 | 40 | 50 | 7UT85
CT1L2 | Resisitance of the relay: Rr: 0
0 | Resisitance of the relay: Rr: CT Ratio:
ABB

## OC+BCPU+FMS-X (2) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV Incomer Transformer Feeder | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core3 |  |  |  | (OC+BCPU+FMS) | [10 empty] | Connected devices: | REC670
REF615
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | FMS
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX
| CT Resistance: |  |  |  |  | Rct< | 10 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 325 |  | V | [12 empty] | #REF!
| Magnetizing Current: |  |  |  |  | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REF615 |  |  |  |  | = | 0.02 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | FMS |  |  |  |  | = | 0.058 |  | VA |  |  | = | 1 | x | 1 | x | 10
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 10 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.175 |  | VA
Non-directional instantaneous and definitive time, phase and residual overcurrent protection
| Ealreq = |  |  | 1.5 | x | Iop | Isr |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[7 empty] | Ipr | [7 empty] | Ir | x | Ir
|  | 6 times rated primary current concidered | [14 empty] | = | 6
|  | The primary operate value (A) | [13 empty] | Iop | = | 15000 |  | A
|  | The rated primary CT current (A) | [13 empty] | Ipr | = | 2500 |  | A
|  | The rated secondary CT current (A) | [13 empty] | Isr | = | 1 |  | A
|  | The rated current of the protection IED (A) | [13 empty] | Ir | = | 1 |  | A
|  | The secondary resistance of the CT (ohm) | [13 empty] | Rct | = | 10 |  | ohm
|  | The resistance of the secondary cable and additional load (ohm). | [13 empty] | RL | = | 1.175 |  | ohm
|  | The burden of an IED current input channel (VA) | [13 empty] | SR | = | 0.02 |  | VA
| Ealreq = |  | 1.5 | x | 15000 |  | x | 1 |  | x | ( | 10 | + | 1.175 | + | 0.02 |  |  | )
[8 empty] | 2500 | [7 empty] | 1 | x | 1
|  | = | 100.76 |  | V
Non-directional inverse time delayed phase and residual overcurrentprotection
| Ealreq = |  |  | 20 | x | Iop | Isr |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[7 empty] | Ipr | [7 empty] | Ir | x | Ir
|  | 1.2 times rated primary current concidered | [14 empty] | = | 1.2
|  | The primary operate value (A) | [13 empty] | Iop | = | 3000 |  | A
|  | The rated primary CT current (A) | [13 empty] | Ipr | = | 2500 |  | A
|  | The rated secondary CT current (A) | [13 empty] | Isr | = | 1 |  | A
|  | The rated current of the protection IED (A) | [13 empty] | Ir | = | 1 |  | A
|  | The secondary resistance of the CT (ohm) | [13 empty] | Rct | = | 10 |  | ohm
|  | The resistance of the secondary cable and additional load (ohm). | [13 empty] | RL | = | 1.175 |  | ohm
|  | The burden of an IED current input channel (VA) | [13 empty] | SR | = | 0.02 |  | VA
| Ealreq = |  | 20 | x | 3000 |  | x | 1 |  | x | ( | 10 | + | 1.175 | + | 0.02 |  |  | )
[8 empty] | 2500 | [7 empty] | 1 | x | 1
|  | = | 268.69 |  | V
|  |  | KPV as per Hitachi recommendation | [7 empty] | Eal | ≥ | max(100.76,268.69) | [9 empty] | ( | max | , | )
[11 empty] | Eal | ≥ | 268.69
[11 empty] | 325 | ≥ | 268.69
[5 empty] | Hence CT is: |  | Suitably Dimensioned
ABB
| T1 |  | Core3 |  |  |  | (OC+BCPU+FMS) | [10 empty] | Connected devices: | REC670
REF615
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | FMS
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [7 empty] | PX
| CT Resistance: | [6 empty] | Rct< | 12 |  | W
| Knee Point Voltage: | [6 empty] | Vk> | 1200 |  | V | [10 empty] | #VALUE!
| Magnetizing Current: | [6 empty] | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REF615 |  |  |  |  | = | 0.02 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | FMS |  |  |  |  | = | 0.058 |  | VA |  |  | = | 1 | x | 1 | x | 12
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 12 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.175 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 15000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 1200 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 12 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | PN | = | ( ( | 1.3 | x | 1200 |  | x | 1 | ) / | 20 | ) - | 12
|  |  | = | 66 |  | VA
ABB
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 15000 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 12 | + | 66 | ) / ( | 12 | + | 1.175 | )
[5 empty] | = | 118.4059
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | 118.4059 |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
ABB
| T1 |  | Core3 |  | #VALUE! x ( (: (OC+BCPU+FMS) |  |  | Connected devices: | REC670
REF615
[5 empty] | #VALUE! x ( (: Tap-1; #VALUE! +: Tap-2; #VALUE! ) / (: Tap-3 |  |  |  | FMS
| CT Ratio: |  |  |  | #VALUE! x ( (: 2500; #VALUE! +: -; #VALUE! ) / (: -; #VALUE! +: /; #VALUE! PL: 1; #VALUE! ): A
Class of Accuracy: | bar: #VALUE! ) / (
| CT Resistance: |  |  |  | #VALUE! PN: Rct<; #VALUE! ) / (: 8; #VALUE! +: W
| Knee Point Voltage: |  |  |  | #VALUE! PN: Vk>; #VALUE! ) / (: 800; #VALUE! +: V | [6 empty] | #VALUE!
| Magnetizing Current: |  |  |  | #VALUE! PN: I0<; #VALUE! ) / (: 75; #VALUE! +: mA at Vk
Other Burdens on same CT core:
| Burden of |  | REC670 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA; #VALUE! +: CT internal Burden
| Burden of |  | REF615 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA; #VALUE! +: PE; #VALUE! PL: =; #VALUE! ): In | x | In | x | Rct
| Burden of |  | FMS |  | #VALUE! PE: =; #VALUE! +: 0.058; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): 1 | x | 1 | x | 8
| Total lead burden |  |  |  | #VALUE! PE: =; #VALUE! +: 1.077; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): 8 |  | VA
| Total lead + other burden |  |  |  | #VALUE! x ( (: PL; #VALUE! PE: =; #VALUE! +: 1.175; #VALUE! ) / (: VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 15000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 800 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 8 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | PN | = | ( ( | 1.3 | x | 800 |  | x | 1 | ) / | 20 | ) - | 8
|  |  | = | 44 | bar: #VALUE! n
ABB
|  |  |  | Required Kssc' | = =: =; #VALUE! n: Itkmax; #VALUE! PE: /; #VALUE! +: Ipn
[5 empty] | = | 15000 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 8 | + | 44 | ) / ( | 8 | + | 1.175 | )
[5 empty] | = | 113.3512
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | 113.3512 |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | #VALUE! n: CT Cable m/mm2; #VALUE! PE: Class; #VALUE! PN: CT Resistance (W) @ 75OC; #VALUE! PE: Limiting Secondary Voltage (Ual), V; #VALUE! PL: Mag. Current (Io), mA at Vk | Relay / Instrument Type |  | CT Suitability
T1 | Core3 |  | 2500 |  | 1 | 120 | 2.5 | PX |  | 10 |  | 325 |  | 50 |  | REC670REF615FMS |  | Suitably Dimensioned
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL

## Main Tariff Meter (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | 33kV Incomer Transformer Feeder | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core4 |  |  | (Main Tariff Meter) | [10 empty] | Connected devices: | EMH
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.2FS5
| CT Resistance: |  |  |  | Rct< | 10 |  | W
| Factor of Safety |  |  |  | FS | 5 | [13 empty] | Suitable Dimensions
| Rated Burden |  |  |  | PN | 10
Other Burdens on same CT core:
| Burden of |  | EMH |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [9 empty] | rec670 | 100A for 1 S
| Burden of |  | 0 |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 10
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 10 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 1.085 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 2500 |  | A
| Internal Burden, | [10 empty] | PE | = | 10 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 1.085 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | Pn | = | 5
| Safety Factor Fs (min) | [11 empty] | = | 20
| XC-RACK = 20 A for 0.5 sec Refer annuxure mail received from manufacturer | [19 empty] | Safety Factor among all connected devices Fs (min)
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 1.085
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 5 | x ( ( | 10 | + | 10 | ) / ( | 10 | + | 1.085 | )
[7 empty] | = | 9.0212
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.085 FS: Total Connected Burden; 1.085 ): …cond.1
[5 empty] | 10 |  | = =: >; 1.085 FS: 1.085; 1.085 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.085 FS: Effective Safety Factor of CT, FS'; 1.085 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.085 FS: 9.0212; 1.085 ): Satisfied
[6 empty] | Hence CT is: | 1.085 FS: Suitable Dimensions
| T1 |  | Core4 |  |  | (Main Tariff Meter) | 1.085 ): Connected devices: | EMH
0
[6 empty] | Tap-1 | 1.085 FS: Tap-2; 1.085 PE: Tap-3
| CT Ratio: |  |  |  |  | 2500 | 1.085 FS: -; 1.085 PE: -; 1.085 PN: /; 1.085 ) / (: 1; 1.085 PE: A
| Class of Accuracy: | [5 empty] | 1.085 FS: 0.2FS5
| CT Resistance: | [5 empty] | = =: Rct<; 1.085 FS: 5; 1.085 PE: W
| Factor of Safety | [5 empty] | = =: FS; 1.085 FS: 10 |  |  | Suitable Dimensions
| Rated Burden | [5 empty] | = =: PN; 1.085 FS: 5; 1.085 PE: VA
Other Burdens on same CT core:
| Burden of |  | EMH |  |  |  | = =: =; 1.085 FS: 0.008; 1.085 PE: VA; 1.085 PN: CT internal Burden
| Burden of |  | 0 |  |  |  | = =: =; 1.085 FS: 0; 1.085 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = =: =; 1.085 FS: 1.077; 1.085 PE: VA; 1.085 ) / (: =; 1.085 PE: 5; 1.085 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.085 FS: 1.085; 1.085 PE: VA
| CT Primary Current, | [5 empty] | 1.085 PN: Ipn; 1.085 ) / (: =; 1.085 PE: -; 1.085 PL: A
| Internal Burden, | [5 empty] | 1.085 PN: PE; 1.085 ) / (: =; 1.085 PE: 5; 1.085 PL: VA
| Burden of CT Leads and burden of connected devices | [5 empty] | 1.085 PN: PL; 1.085 ) / (: =; 1.085 PE: 1.085; 1.085 PL: VA
| Rated Secondary Current, | [5 empty] | 1.085 PN: In; 1.085 ) / (: =; 1.085 PE: 1; 1.085 PL: A
| CT Safety Factor | [5 empty] | 1.085 PN: n; 1.085 ) / (: =; 1.085 PE: 10
| Safety Factor among all connected devices Fs (min) | [5 empty] | 1.085 ) / (: =; 1.085 PE: 20; 1.085 PL: **; 1.085 ): Assumed
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.085 +: Fs(min); 1.085 PL: =; 1.085 ): 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.085 FS: Connected devices burden; 1.085 PE: +; 1.085 +: Lead Burden
[7 empty] | = | 1.085
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 10 | x ( ( | 5 | + | 5 | ) / ( | 5 | + | 1.085 | )
[7 empty] | = | 16.4338
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.085 FS: Total Connected Burden; 1.085 ): …cond.1
[5 empty] | 5 |  | = =: >; 1.085 FS: 1.085; 1.085 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.085 FS: Effective Safety Factor of CT, FS'; 1.085 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.085 FS: 16.4338; 1.085 ): Satisfied
[6 empty] | Hence CT is: | 1.085 FS: Suitable Dimensions
| T1 |  | Core4 |  |  | (Main Tariff Meter)
0
[6 empty] | Tap-1 | 1.085 FS: Tap-2; 1.085 PE: Tap-3
| CT Ratio: |  |  |  |  | 2500 | 1.085 FS: -; 1.085 PE: -; 1.085 PN: /; 1.085 ) / (: 1; 1.085 PE: A
| Class of Accuracy: | [5 empty] | 1.085 PE: 0.2FS5
| CT Resistance: | [5 empty] | 1.085 x ( (: Rct<; 1.085 PE: -; 1.085 PN: W
| Factor of Safety | [18 empty] | #VALUE! | bar: 1.085 x ( ( to 1.085 +
| Rated Burden | [5 empty] | 1.085 x ( (: PN; 1.085 PE: -; 1.085 PN: VA
Other Burdens on same CT core:
| Burden of |  | EMH |  |  |  | = =: =; 1.085 FS: 0.008; 1.085 PE: VA; 1.085 PN: CT internal Burden
| Burden of |  | 0 |  |  |  | = =: =; 1.085 FS: 0; 1.085 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [5 empty] | = =: =; 1.085 FS: 1.077; 1.085 PE: VA; 1.085 ) / (: =; 1.085 PE: #VALUE!; 1.085 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.085 FS: 1.085; 1.085 PE: VA
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.085 +: Fs(min); 1.085 PL: =; 1.085 ): 20
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.085 FS: CT Int. Burden; 1.085 +: +; 1.085 PN: Connected Burden
[7 empty] | = | #VALUE! |  | + | 1.085
[7 empty] | = | #VALUE!
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | - | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 1.085 | )
[7 empty] | = | #VALUE!
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; #VALUE! FS: Total Connected Burden; #VALUE! ): …cond.1
[5 empty] | - |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; #VALUE! FS: Effective Safety Factor of CT, FS'; #VALUE! ): …cond.2
[5 empty] | 20 |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
[6 empty] | Hence CT is: | #VALUE! FS: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; #VALUE! x ( (: CT Resistance (W) @ 75OC; #VALUE! +: Rated Burden VA; #VALUE! +: Relay / Instrument Type; #VALUE! ): CT Suitability
T1 | Core4 |  | 2500 | 1 | 120 | 6 | = =: 0.2FS5; #VALUE! x ( (: 10; #VALUE! +: 10; #VALUE! ) / (: -; #VALUE! +: EMH; #VALUE! ): Suitable Dimensions
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )

## Check Tariff Meter + Ammeters (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | 33kV Incomer Transformer Feeder | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core5 |  |  | (Check Tariff Meter + Ammeters) | [10 empty] | Connected devices: | XC-RACK
POINTER
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.2FS5
| CT Resistance: |  |  |  | Rct< | 10 |  | W
| Factor of Safety |  |  |  | FS | 5 | [13 empty] | Suitable Dimensions
| Rated Burden |  |  |  | PN | 10
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [9 empty] | rec670 | 100A for 1 S
| Burden of |  | POINTER |  |  |  | = | 1.25 |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 10
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 10 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 2.335 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 2500 |  | A
| Internal Burden, | [10 empty] | PE | = | 10 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 2.335 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | n | = | 5
| Safety Factor Fs (min) | [11 empty] | = | 20 | [6 empty] | Safety Factor among all connected devices Fs (min)
XC-RACK = 20 A for 0.5 sec Refer annuxure mail received from manufacturer
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 2.335
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 5 | x ( ( | 10 | + | 10 | ) / ( | 10 | + | 2.335 | )
[7 empty] | = | 8.107
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 2.335 FS: Total Connected Burden; 2.335 ): …cond.1
[5 empty] | 10 |  | = =: >; 2.335 FS: 2.335; 2.335 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 2.335 FS: Effective Safety Factor of CT, FS'; 2.335 ): …cond.2
[5 empty] | 20 |  | = =: >; 2.335 FS: 8.107; 2.335 ): Satisfied
[6 empty] | Hence CT is: | 2.335 FS: Suitable Dimensions
| T1 |  | Core5 |  |  | (Check Tariff Meter + Ammeters) | 2.335 ): Connected devices: | XC-RACK
0
[6 empty] | Tap-1 | 2.335 FS: Tap-2; 2.335 PE: Tap-3
| CT Ratio: |  |  |  |  | 2500 | 2.335 FS: -; 2.335 PE: -; 2.335 PN: /; 2.335 ) / (: 1; 2.335 PE: A
| Class of Accuracy: | [5 empty] | 2.335 FS: 0.2FS5
| CT Resistance: | [5 empty] | = =: Rct<; 2.335 FS: 5; 2.335 PE: W
| Factor of Safety | [5 empty] | = =: FS; 2.335 FS: 10 |  |  | Suitable Dimensions
| Rated Burden | [5 empty] | = =: PN; 2.335 FS: 5; 2.335 PE: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 2.335 FS: 0.008; 2.335 PE: VA; 2.335 PN: CT internal Burden
| Burden of |  | POINTER |  |  |  | = =: =; 2.335 FS: 1.25; 2.335 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = =: =; 2.335 FS: 1.077; 2.335 PE: VA; 2.335 ) / (: =; 2.335 PE: 5; 2.335 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 2.335 FS: 2.335; 2.335 PE: VA
| CT Primary Current, | [5 empty] | 2.335 PN: Ipn; 2.335 ) / (: =; 2.335 PE: -; 2.335 PL: A
| Internal Burden, | [5 empty] | 2.335 PN: PE; 2.335 ) / (: =; 2.335 PE: 5; 2.335 PL: VA
| Burden of CT Leads and burden of connected devices | [5 empty] | 2.335 PN: PL; 2.335 ) / (: =; 2.335 PE: 2.335; 2.335 PL: VA
| Rated Secondary Current, | [5 empty] | 2.335 PN: In; 2.335 ) / (: =; 2.335 PE: 1; 2.335 PL: A
| CT Safety Factor | [5 empty] | 2.335 PN: n; 2.335 ) / (: =; 2.335 PE: 10
| Safety Factor among all connected devices Fs (min) | [5 empty] | 2.335 ) / (: =; 2.335 PE: 20; 2.335 PL: **; 2.335 ): Assumed
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 2.335 +: Fs(min); 2.335 PL: =; 2.335 ): 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = =: =; 2.335 FS: Connected devices burden; 2.335 PE: +; 2.335 +: Lead Burden
[7 empty] | = | 2.335
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 10 | x ( ( | 5 | + | 5 | ) / ( | 5 | + | 2.335 | )
[7 empty] | = | 13.6332
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 2.335 FS: Total Connected Burden; 2.335 ): …cond.1
[5 empty] | 5 |  | = =: >; 2.335 FS: 2.335; 2.335 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 2.335 FS: Effective Safety Factor of CT, FS'; 2.335 ): …cond.2
[5 empty] | 20 |  | = =: >; 2.335 FS: 13.6332; 2.335 ): Satisfied
[6 empty] | Hence CT is: | 2.335 FS: Suitable Dimensions
| T1 |  | Core5 |  |  | (Check Tariff Meter + Ammeters)
0
[6 empty] | Tap-1 | 2.335 FS: Tap-2; 2.335 PE: Tap-3
| CT Ratio: |  |  |  |  | 2500 | 2.335 FS: -; 2.335 PE: -; 2.335 PN: /; 2.335 ) / (: 1; 2.335 PE: A
| Class of Accuracy: | [5 empty] | 2.335 PE: 0.2FS5
| CT Resistance: | [5 empty] | 2.335 x ( (: Rct<; 2.335 PE: -; 2.335 PN: W
| Factor of Safety | [18 empty] | #VALUE! | bar: 2.335 x ( ( to 2.335 +
| Rated Burden | [5 empty] | 2.335 x ( (: PN; 2.335 PE: -; 2.335 PN: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 2.335 FS: 0.008; 2.335 PE: VA; 2.335 PN: CT internal Burden
| Burden of |  | POINTER |  |  |  | = =: =; 2.335 FS: 1.25; 2.335 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [5 empty] | = =: =; 2.335 FS: 1.077; 2.335 PE: VA; 2.335 ) / (: =; 2.335 PE: #VALUE!; 2.335 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 2.335 FS: 2.335; 2.335 PE: VA
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 2.335 +: Fs(min); 2.335 PL: =; 2.335 ): 20
|  | Total connected burden on CT |  |  |  |  | = =: =; 2.335 FS: CT Int. Burden; 2.335 +: +; 2.335 PN: Connected Burden
[7 empty] | = | #VALUE! |  | + | 2.335
[7 empty] | = | #VALUE!
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | - | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 2.335 | )
[7 empty] | = | #VALUE!
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; #VALUE! FS: Total Connected Burden; #VALUE! ): …cond.1
[5 empty] | - |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; #VALUE! FS: Effective Safety Factor of CT, FS'; #VALUE! ): …cond.2
[5 empty] | 20 |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
[6 empty] | Hence CT is: | #VALUE! FS: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; #VALUE! x ( (: CT Resistance (W) @ 75OC; #VALUE! +: Rated Burden VA; #VALUE! +: Relay / Instrument Type; #VALUE! ): CT Suitability
T1 | Core5 |  | 2500 | 1 | 120 | 6 | = =: 0.2FS5; #VALUE! x ( (: 10; #VALUE! +: 10; #VALUE! ) / (: -; #VALUE! +: XC-RACK POINTER; #VALUE! ): Suitable Dimensions
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )

## 5 (7) (hidden)
33kV Station Transformer (H03,H27)
Back to
INDEX

## OC+BCPU+FMS-X (3) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV Station Transformer Feeder | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core1 |  |  |  | (OC+BCPU+FMS) | [10 empty] | Connected devices: | REC670
REF615
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | FMS
| CT Ratio: | [5 empty] | 100 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX
| CT Resistance: |  |  |  |  | Rct< | 0.32 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 145 |  | V | [12 empty] | #REF!
| Magnetizing Current: |  |  |  |  | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REF615 |  |  |  |  | = | 0.02 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | FMS |  |  |  |  | = | 0.058 |  | VA |  |  | = | 1 | x | 1 | x | 0.32
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 0.32 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.175 |  | VA
Non-directional instantaneous and definitive time, phase and residual overcurrent protection
| Ealreq = |  |  | 1.5 | x | Iop | Isr |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[7 empty] | Ipr | [7 empty] | Ir | x | Ir
|  | 6 times rated primary current concidered | [14 empty] | = | 6
|  | The primary operate value (A) | [13 empty] | Iop | = | 600 |  | A
|  | The rated primary CT current (A) | [13 empty] | Ipr | = | 100 |  | A
|  | The rated secondary CT current (A) | [13 empty] | Isr | = | 1 |  | A
|  | The rated current of the protection IED (A) | [13 empty] | Ir | = | 1 |  | A
|  | The secondary resistance of the CT (ohm) | [13 empty] | Rct | = | 0.32 |  | ohm
|  | The resistance of the secondary cable and additional load (ohm). | [13 empty] | RL | = | 1.175 |  | ohm
|  | The burden of an IED current input channel (VA) | [13 empty] | SR | = | 0.02 |  | VA
| Ealreq = |  | 1.5 | x | 600 |  | x | 1 |  | x | ( | 0.32 | + | 1.175 | + | 0.02 |  |  | )
[8 empty] | 100 | [7 empty] | 1 | x | 1
|  | = | 13.64 |  | V
Non-directional inverse time delayed phase and residual overcurrentprotection
| Ealreq = |  |  | 20 | x | Iop | Isr |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[7 empty] | Ipr | [7 empty] | Ir | x | Ir
|  | 1.2 times rated primary current concidered | [14 empty] | = | 1.2
|  | The primary operate value (A) | [13 empty] | Iop | = | 120 |  | A
|  | The rated primary CT current (A) | [13 empty] | Ipr | = | 100 |  | A
|  | The rated secondary CT current (A) | [13 empty] | Isr | = | 1 |  | A
|  | The rated current of the protection IED (A) | [13 empty] | Ir | = | 1 |  | A
|  | The secondary resistance of the CT (ohm) | [13 empty] | Rct | = | 0.32 |  | ohm
|  | The resistance of the secondary cable and additional load (ohm). | [13 empty] | RL | = | 1.175 |  | ohm
|  | The burden of an IED current input channel (VA) | [13 empty] | SR | = | 0.02 |  | VA
| Ealreq = |  | 20 | x | 120 |  | x | 1 |  | x | ( | 0.32 | + | 1.175 | + | 0.02 |  |  | )
[8 empty] | 100 | [7 empty] | 1 | x | 1
|  | = | 36.37 |  | V
|  |  | KPV as per Hitachi recommendation | [7 empty] | Eal | ≥ | max(13.64,36.37) | [9 empty] | ( | max | , | )
[11 empty] | Eal | ≥ | 36.37
[11 empty] | 145 | ≥ | 36.37
[5 empty] | Hence CT is: |  | Suitably Dimensioned
ABB
| T1 |  | Core1 |  |  |  | (OC+BCPU+FMS) | [10 empty] | Connected devices: | REC670
REF615
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | FMS
| CT Ratio: | [5 empty] | 100 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [7 empty] | PX
| CT Resistance: | [6 empty] | Rct< | 12 |  | W
| Knee Point Voltage: | [6 empty] | Vk> | 1200 |  | V | [10 empty] | #VALUE!
| Magnetizing Current: | [6 empty] | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REF615 |  |  |  |  | = | 0.02 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | FMS |  |  |  |  | = | 0.058 |  | VA |  |  | = | 1 | x | 1 | x | 12
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 12 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.175 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 600 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 1200 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 12 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | PN | = | ( ( | 1.3 | x | 1200 |  | x | 1 | ) / | 20 | ) - | 12
|  |  | = | 66 |  | VA
ABB
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 600 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 12 | + | 66 | ) / ( | 12 | + | 1.175 | )
[5 empty] | = | 118.4059
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | 118.4059 |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
ABB
| T1 |  | Core1 |  | #VALUE! x ( (: (OC+BCPU+FMS) |  |  | Connected devices: | REC670
REF615
[5 empty] | #VALUE! x ( (: Tap-1; #VALUE! +: Tap-2; #VALUE! ) / (: Tap-3 |  |  |  | FMS
| CT Ratio: |  |  |  | #VALUE! x ( (: 100; #VALUE! +: -; #VALUE! ) / (: -; #VALUE! +: /; #VALUE! PL: 1; #VALUE! ): A
Class of Accuracy: | bar: #VALUE! ) / (
| CT Resistance: |  |  |  | #VALUE! PN: Rct<; #VALUE! ) / (: 8; #VALUE! +: W
| Knee Point Voltage: |  |  |  | #VALUE! PN: Vk>; #VALUE! ) / (: 800; #VALUE! +: V | [6 empty] | #VALUE!
| Magnetizing Current: |  |  |  | #VALUE! PN: I0<; #VALUE! ) / (: 75; #VALUE! +: mA at Vk
Other Burdens on same CT core:
| Burden of |  | REC670 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA; #VALUE! +: CT internal Burden
| Burden of |  | REF615 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA; #VALUE! +: PE; #VALUE! PL: =; #VALUE! ): In | x | In | x | Rct
| Burden of |  | FMS |  | #VALUE! PE: =; #VALUE! +: 0.058; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): 1 | x | 1 | x | 8
| Total lead burden |  |  |  | #VALUE! PE: =; #VALUE! +: 1.077; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): 8 |  | VA
| Total lead + other burden |  |  |  | #VALUE! x ( (: PL; #VALUE! PE: =; #VALUE! +: 1.175; #VALUE! ) / (: VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 600 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 800 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 8 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | PN | = | ( ( | 1.3 | x | 800 |  | x | 1 | ) / | 20 | ) - | 8
|  |  | = | 44 | bar: #VALUE! n
ABB
|  |  |  | Required Kssc' | = =: =; #VALUE! n: Itkmax; #VALUE! PE: /; #VALUE! +: Ipn
[5 empty] | = | 600 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 8 | + | 44 | ) / ( | 8 | + | 1.175 | )
[5 empty] | = | 113.3512
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | 113.3512 |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | #VALUE! n: CT Cable m/mm2; #VALUE! PE: Class; #VALUE! PN: CT Resistance (W) @ 75OC; #VALUE! PE: Limiting Secondary Voltage (Ual), V; #VALUE! PL: Mag. Current (Io), mA at Vk | Relay / Instrument Type |  | CT Suitability
T1 | Core1 |  | 100 |  | 1 | 120 | 6 | PX |  | 0.32 |  | 145 |  | 50 |  | REC670REF615FMS |  | Suitably Dimensioned
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL

## (Metering + Ammeter) (2) (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | 33kV Station Transformer Feeder | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core2 |  |  | (Metering + Ammeter) | [10 empty] | Connected devices: | XC-RACK
POINTER
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 100 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.5FS5
| CT Resistance: |  |  |  | Rct< | 1 |  | W
| Factor of Safety |  |  |  | FS | 5 | [13 empty] | Suitable Dimensions
| Rated Burden |  |  |  | PN | 5
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [8 empty] | rec670 | 100A for 1 S
| Burden of |  | POINTER |  |  |  | = | 1.25 |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 1
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 1 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 2.335 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 100 |  | A
| Internal Burden, | [10 empty] | PE | = | 1 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 2.335 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | n | = | 5
| Safety Factor Fs (min) | [11 empty] | = | 20
XC-RACK = 20 A for 0.5 sec Refer annuxure mail received from manufacturer
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 2.335
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 5 | x ( ( | 1 | + | 5 | ) / ( | 1 | + | 2.335 | )
[7 empty] | = | 8.9954
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 2.335 FS: Total Connected Burden; 2.335 ): …cond.1
[5 empty] | 5 |  | = =: >; 2.335 FS: 2.335; 2.335 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 2.335 FS: Effective Safety Factor of CT, FS'; 2.335 ): …cond.2
[5 empty] | 20 |  | = =: >; 2.335 FS: 8.9954; 2.335 ): Satisfied
[6 empty] | Hence CT is: | 2.335 FS: Suitable Dimensions
| T1 |  | Core2 |  |  | (Metering + Ammeter) | 2.335 ): Connected devices: | XC-RACK
0
[6 empty] | Tap-1 | 2.335 FS: Tap-2; 2.335 PE: Tap-3
| CT Ratio: |  |  |  |  | 100 | 2.335 FS: -; 2.335 PE: -; 2.335 PN: /; 2.335 ) / (: 1; 2.335 PE: A
| Class of Accuracy: | [5 empty] | 2.335 FS: 0.5FS5
| CT Resistance: | [5 empty] | = =: Rct<; 2.335 FS: 5; 2.335 PE: W
| Factor of Safety | [5 empty] | = =: FS; 2.335 FS: 10 |  |  | Suitable Dimensions
| Rated Burden | [5 empty] | = =: PN; 2.335 FS: 5; 2.335 PE: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 2.335 FS: 0.008; 2.335 PE: VA; 2.335 PN: CT internal Burden
| Burden of |  | POINTER |  |  |  | = =: =; 2.335 FS: 1.25; 2.335 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = =: =; 2.335 FS: 1.077; 2.335 PE: VA; 2.335 ) / (: =; 2.335 PE: 5; 2.335 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 2.335 FS: 2.335; 2.335 PE: VA
| CT Primary Current, | [5 empty] | 2.335 PN: Ipn; 2.335 ) / (: =; 2.335 PE: -; 2.335 PL: A
| Internal Burden, | [5 empty] | 2.335 PN: PE; 2.335 ) / (: =; 2.335 PE: 5; 2.335 PL: VA
| Burden of CT Leads and burden of connected devices | [5 empty] | 2.335 PN: PL; 2.335 ) / (: =; 2.335 PE: 2.335; 2.335 PL: VA
| Rated Secondary Current, | [5 empty] | 2.335 PN: In; 2.335 ) / (: =; 2.335 PE: 1; 2.335 PL: A
| CT Safety Factor | [5 empty] | 2.335 PN: n; 2.335 ) / (: =; 2.335 PE: 10
| Safety Factor among all connected devices Fs (min) | [5 empty] | 2.335 ) / (: =; 2.335 PE: 20; 2.335 PL: **; 2.335 ): Assumed
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 2.335 +: Fs(min); 2.335 PL: =; 2.335 ): 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = =: =; 2.335 FS: Connected devices burden; 2.335 PE: +; 2.335 +: Lead Burden
[7 empty] | = | 2.335
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 10 | x ( ( | 5 | + | 5 | ) / ( | 5 | + | 2.335 | )
[7 empty] | = | 13.6332
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 2.335 FS: Total Connected Burden; 2.335 ): …cond.1
[5 empty] | 5 |  | = =: >; 2.335 FS: 2.335; 2.335 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 2.335 FS: Effective Safety Factor of CT, FS'; 2.335 ): …cond.2
[5 empty] | 20 |  | = =: >; 2.335 FS: 13.6332; 2.335 ): Satisfied
[6 empty] | Hence CT is: | 2.335 FS: Suitable Dimensions
| T1 |  | Core2 |  |  | (Metering + Ammeter)
0
[6 empty] | Tap-1 | 2.335 FS: Tap-2; 2.335 PE: Tap-3
| CT Ratio: |  |  |  |  | 100 | 2.335 FS: -; 2.335 PE: -; 2.335 PN: /; 2.335 ) / (: 1; 2.335 PE: A
| Class of Accuracy: | [5 empty] | 2.335 PE: 0.5FS5
| CT Resistance: | [5 empty] | 2.335 x ( (: Rct<; 2.335 PE: -; 2.335 PN: W
| Factor of Safety | [18 empty] | #VALUE! | bar: 2.335 x ( ( to 2.335 +
| Rated Burden | [5 empty] | 2.335 x ( (: PN; 2.335 PE: -; 2.335 PN: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 2.335 FS: 0.008; 2.335 PE: VA; 2.335 PN: CT internal Burden
| Burden of |  | POINTER |  |  |  | = =: =; 2.335 FS: 1.25; 2.335 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [5 empty] | = =: =; 2.335 FS: 1.077; 2.335 PE: VA; 2.335 ) / (: =; 2.335 PE: #VALUE!; 2.335 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 2.335 FS: 2.335; 2.335 PE: VA
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 2.335 +: Fs(min); 2.335 PL: =; 2.335 ): 20
|  | Total connected burden on CT |  |  |  |  | = =: =; 2.335 FS: CT Int. Burden; 2.335 +: +; 2.335 PN: Connected Burden
[7 empty] | = | #VALUE! |  | + | 2.335
[7 empty] | = | #VALUE!
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | - | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 2.335 | )
[7 empty] | = | #VALUE!
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; #VALUE! FS: Total Connected Burden; #VALUE! ): …cond.1
[5 empty] | - |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; #VALUE! FS: Effective Safety Factor of CT, FS'; #VALUE! ): …cond.2
[5 empty] | 20 |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
[6 empty] | Hence CT is: | #VALUE! FS: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; #VALUE! x ( (: CT Resistance (W) @ 75OC; #VALUE! +: Rated Burden VA; #VALUE! +: Relay / Instrument Type; #VALUE! ): CT Suitability
T1 | Core2 |  | 100 | 1 | 120 | 6 | = =: 0.5FS5; #VALUE! x ( (: 1; #VALUE! +: 5; #VALUE! ) / (: -; #VALUE! +: XC-RACK POINTER; #VALUE! ): Suitable Dimensions
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )

## 5 (8) (hidden)
33kV BC & BS (H06,H14,H22)
Back to
INDEX

## OC+BCPU+FMS-X (4) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV BC & BS Feeder | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core1 |  |  |  | (OC+BCPU+FMS) | [10 empty] | Connected devices: | REC670
REF615
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | FMS
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX
| CT Resistance: |  |  |  |  | Rct< | 10 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 325 |  | V | [12 empty] | #REF!
| Magnetizing Current: |  |  |  |  | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REF615 |  |  |  |  | = | 0.02 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | FMS |  |  |  |  | = | 0.058 |  | VA |  |  | = | 1 | x | 1 | x | 10
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 10 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.175 |  | VA
Non-directional instantaneous and definitive time, phase and residual overcurrent protection
| Ealreq = |  |  | 1.5 | x | Iop | Isr |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[7 empty] | Ipr | [7 empty] | Ir | x | Ir
|  | 6 times rated primary current concidered | [14 empty] | = | 6
|  | The primary operate value (A) | [13 empty] | Iop | = | 15000 |  | A
|  | The rated primary CT current (A) | [13 empty] | Ipr | = | 2500 |  | A
|  | The rated secondary CT current (A) | [13 empty] | Isr | = | 1 |  | A
|  | The rated current of the protection IED (A) | [13 empty] | Ir | = | 1 |  | A
|  | The secondary resistance of the CT (ohm) | [13 empty] | Rct | = | 10 |  | ohm
|  | The resistance of the secondary cable and additional load (ohm). | [13 empty] | RL | = | 1.175 |  | ohm
|  | The burden of an IED current input channel (VA) | [13 empty] | SR | = | 0.02 |  | VA
| Ealreq = |  | 1.5 | x | 15000 |  | x | 1 |  | x | ( | 10 | + | 1.175 | + | 0.02 |  |  | )
[8 empty] | 2500 | [7 empty] | 1 | x | 1
|  | = | 100.76 |  | V
Non-directional inverse time delayed phase and residual overcurrentprotection
| Ealreq = |  |  | 20 | x | Iop | Isr |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[7 empty] | Ipr | [7 empty] | Ir | x | Ir
|  | 1.2 times rated primary current concidered | [14 empty] | = | 1.2
|  | The primary operate value (A) | [13 empty] | Iop | = | 3000 |  | A
|  | The rated primary CT current (A) | [13 empty] | Ipr | = | 2500 |  | A
|  | The rated secondary CT current (A) | [13 empty] | Isr | = | 1 |  | A
|  | The rated current of the protection IED (A) | [13 empty] | Ir | = | 1 |  | A
|  | The secondary resistance of the CT (ohm) | [13 empty] | Rct | = | 10 |  | ohm
|  | The resistance of the secondary cable and additional load (ohm). | [13 empty] | RL | = | 1.175 |  | ohm
|  | The burden of an IED current input channel (VA) | [13 empty] | SR | = | 0.02 |  | VA
| Ealreq = |  | 20 | x | 3000 |  | x | 1 |  | x | ( | 10 | + | 1.175 | + | 0.02 |  |  | )
[8 empty] | 2500 | [7 empty] | 1 | x | 1
|  | = | 268.69 |  | V
|  |  | KPV as per Hitachi recommendation | [7 empty] | Eal | ≥ | max(100.76,268.69) | [9 empty] | ( | max | , | )
[11 empty] | Eal | ≥ | 268.69
[11 empty] | 325 | ≥ | 268.69
[5 empty] | Hence CT is: |  | Suitably Dimensioned
ABB
| T1 |  | Core1 |  |  |  | (OC+BCPU+FMS) | [10 empty] | Connected devices: | REC670
REF615
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | FMS
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [7 empty] | PX
| CT Resistance: | [6 empty] | Rct< | 12 |  | W
| Knee Point Voltage: | [6 empty] | Vk> | 1200 |  | V | [10 empty] | #VALUE!
| Magnetizing Current: | [6 empty] | I0< | 50 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REF615 |  |  |  |  | = | 0.02 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | FMS |  |  |  |  | = | 0.058 |  | VA |  |  | = | 1 | x | 1 | x | 12
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 12 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.175 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 15000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 1200 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 12 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | PN | = | ( ( | 1.3 | x | 1200 |  | x | 1 | ) / | 20 | ) - | 12
|  |  | = | 66 |  | VA
ABB
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 15000 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 12 | + | 66 | ) / ( | 12 | + | 1.175 | )
[5 empty] | = | 118.4059
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | 118.4059 |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
ABB
| T1 |  | Core1 |  | #VALUE! x ( (: (OC+BCPU+FMS) |  |  | Connected devices: | REC670
REF615
[5 empty] | #VALUE! x ( (: Tap-1; #VALUE! +: Tap-2; #VALUE! ) / (: Tap-3 |  |  |  | FMS
| CT Ratio: |  |  |  | #VALUE! x ( (: 2500; #VALUE! +: -; #VALUE! ) / (: -; #VALUE! +: /; #VALUE! PL: 1; #VALUE! ): A
Class of Accuracy: | bar: #VALUE! ) / (
| CT Resistance: |  |  |  | #VALUE! PN: Rct<; #VALUE! ) / (: 8; #VALUE! +: W
| Knee Point Voltage: |  |  |  | #VALUE! PN: Vk>; #VALUE! ) / (: 800; #VALUE! +: V | [6 empty] | #VALUE!
| Magnetizing Current: |  |  |  | #VALUE! PN: I0<; #VALUE! ) / (: 75; #VALUE! +: mA at Vk
Other Burdens on same CT core:
| Burden of |  | REC670 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA; #VALUE! +: CT internal Burden
| Burden of |  | REF615 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA; #VALUE! +: PE; #VALUE! PL: =; #VALUE! ): In | x | In | x | Rct
| Burden of |  | FMS |  | #VALUE! PE: =; #VALUE! +: 0.058; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): 1 | x | 1 | x | 8
| Total lead burden |  |  |  | #VALUE! PE: =; #VALUE! +: 1.077; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): 8 |  | VA
| Total lead + other burden |  |  |  | #VALUE! x ( (: PL; #VALUE! PE: =; #VALUE! +: 1.175; #VALUE! ) / (: VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 15000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 800 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 8 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | PN | = | ( ( | 1.3 | x | 800 |  | x | 1 | ) / | 20 | ) - | 8
|  |  | = | 44 | bar: #VALUE! n
ABB
|  |  |  | Required Kssc' | = =: =; #VALUE! n: Itkmax; #VALUE! PE: /; #VALUE! +: Ipn
[5 empty] | = | 15000 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 8 | + | 44 | ) / ( | 8 | + | 1.175 | )
[5 empty] | = | 113.3512
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | 113.3512 |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | #VALUE! n: CT Cable m/mm2; #VALUE! PE: Class; #VALUE! PN: CT Resistance (W) @ 75OC; #VALUE! PE: Limiting Secondary Voltage (Ual), V; #VALUE! PL: Mag. Current (Io), mA at Vk | Relay / Instrument Type |  | CT Suitability
T1 | Core1 |  | 2500 |  | 1 | 120 | 2.5 | PX |  | 10 |  | 325 |  | 50 |  | REC670REF615FMS |  | Suitably Dimensioned
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL

## (Metering + Ammeter) (3) (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | 33kV BC & BS Feeder | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core2 |  |  | (Metering + Ammeter) | [10 empty] | Connected devices: | XC-RACK
POINTER
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.5FS5
| CT Resistance: |  |  |  | Rct< | 10 |  | W
| Factor of Safety |  |  |  | FS | 5 | [13 empty] | Suitable Dimensions
| Rated Burden |  |  |  | PN | 7.5
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [8 empty] | rec670 | 100A for 1 S
| Burden of |  | POINTER |  |  |  | = | 1.25 |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 10
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 10 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 2.335 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 2500 |  | A
| Internal Burden, | [10 empty] | PE | = | 10 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 2.335 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | n | = | 10
| Safety Factor Fs (min) | [11 empty] | = | 20
XC-RACK = 20 A for 0.5 sec Refer annuxure mail received from manufacturer
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 2.335
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 5 | x ( ( | 10 | + | 7.5 | ) / ( | 10 | + | 2.335 | )
[7 empty] | = | 7.0936
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 2.335 FS: Total Connected Burden; 2.335 ): …cond.1
[5 empty] | 7.5 |  | = =: >; 2.335 FS: 2.335; 2.335 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 2.335 FS: Effective Safety Factor of CT, FS'; 2.335 ): …cond.2
[5 empty] | 20 |  | = =: >; 2.335 FS: 7.0936; 2.335 ): Satisfied
[6 empty] | Hence CT is: | 2.335 FS: Suitable Dimensions
| T1 |  | Core2 |  |  | (Metering + Ammeter) | 2.335 ): Connected devices: | XC-RACK
0
[6 empty] | Tap-1 | 2.335 FS: Tap-2; 2.335 PE: Tap-3
| CT Ratio: |  |  |  |  | 2500 | 2.335 FS: -; 2.335 PE: -; 2.335 PN: /; 2.335 ) / (: 1; 2.335 PE: A
| Class of Accuracy: | [5 empty] | 2.335 FS: 0.5FS5
| CT Resistance: | [5 empty] | = =: Rct<; 2.335 FS: 5; 2.335 PE: W
| Factor of Safety | [5 empty] | = =: FS; 2.335 FS: 10 |  |  | Suitable Dimensions
| Rated Burden | [5 empty] | = =: PN; 2.335 FS: 5; 2.335 PE: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 2.335 FS: 0.008; 2.335 PE: VA; 2.335 PN: CT internal Burden
| Burden of |  | POINTER |  |  |  | = =: =; 2.335 FS: 1.25; 2.335 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = =: =; 2.335 FS: 1.077; 2.335 PE: VA; 2.335 ) / (: =; 2.335 PE: 5; 2.335 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 2.335 FS: 2.335; 2.335 PE: VA
| CT Primary Current, | [5 empty] | 2.335 PN: Ipn; 2.335 ) / (: =; 2.335 PE: -; 2.335 PL: A
| Internal Burden, | [5 empty] | 2.335 PN: PE; 2.335 ) / (: =; 2.335 PE: 5; 2.335 PL: VA
| Burden of CT Leads and burden of connected devices | [5 empty] | 2.335 PN: PL; 2.335 ) / (: =; 2.335 PE: 2.335; 2.335 PL: VA
| Rated Secondary Current, | [5 empty] | 2.335 PN: In; 2.335 ) / (: =; 2.335 PE: 1; 2.335 PL: A
| CT Safety Factor | [5 empty] | 2.335 PN: n; 2.335 ) / (: =; 2.335 PE: 10
| Safety Factor among all connected devices Fs (min) | [5 empty] | 2.335 ) / (: =; 2.335 PE: 20; 2.335 PL: **; 2.335 ): Assumed
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 2.335 +: Fs(min); 2.335 PL: =; 2.335 ): 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = =: =; 2.335 FS: Connected devices burden; 2.335 PE: +; 2.335 +: Lead Burden
[7 empty] | = | 2.335
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 10 | x ( ( | 5 | + | 5 | ) / ( | 5 | + | 2.335 | )
[7 empty] | = | 13.6332
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 2.335 FS: Total Connected Burden; 2.335 ): …cond.1
[5 empty] | 5 |  | = =: >; 2.335 FS: 2.335; 2.335 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 2.335 FS: Effective Safety Factor of CT, FS'; 2.335 ): …cond.2
[5 empty] | 20 |  | = =: >; 2.335 FS: 13.6332; 2.335 ): Satisfied
[6 empty] | Hence CT is: | 2.335 FS: Suitable Dimensions
| T1 |  | Core2 |  |  | (Metering + Ammeter)
0
[6 empty] | Tap-1 | 2.335 FS: Tap-2; 2.335 PE: Tap-3
| CT Ratio: |  |  |  |  | 2500 | 2.335 FS: -; 2.335 PE: -; 2.335 PN: /; 2.335 ) / (: 1; 2.335 PE: A
| Class of Accuracy: | [5 empty] | 2.335 PE: 0.5FS5
| CT Resistance: | [5 empty] | 2.335 x ( (: Rct<; 2.335 PE: -; 2.335 PN: W
| Factor of Safety | [18 empty] | #VALUE! | bar: 2.335 x ( ( to 2.335 +
| Rated Burden | [5 empty] | 2.335 x ( (: PN; 2.335 PE: -; 2.335 PN: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 2.335 FS: 0.008; 2.335 PE: VA; 2.335 PN: CT internal Burden
| Burden of |  | POINTER |  |  |  | = =: =; 2.335 FS: 1.25; 2.335 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [5 empty] | = =: =; 2.335 FS: 1.077; 2.335 PE: VA; 2.335 ) / (: =; 2.335 PE: #VALUE!; 2.335 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 2.335 FS: 2.335; 2.335 PE: VA
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 2.335 +: Fs(min); 2.335 PL: =; 2.335 ): 20
|  | Total connected burden on CT |  |  |  |  | = =: =; 2.335 FS: CT Int. Burden; 2.335 +: +; 2.335 PN: Connected Burden
[7 empty] | = | #VALUE! |  | + | 2.335
[7 empty] | = | #VALUE!
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | - | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 2.335 | )
[7 empty] | = | #VALUE!
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; #VALUE! FS: Total Connected Burden; #VALUE! ): …cond.1
[5 empty] | - |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; #VALUE! FS: Effective Safety Factor of CT, FS'; #VALUE! ): …cond.2
[5 empty] | 20 |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
[6 empty] | Hence CT is: | #VALUE! FS: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; #VALUE! x ( (: CT Resistance (W) @ 75OC; #VALUE! +: Rated Burden VA; #VALUE! +: Relay / Instrument Type; #VALUE! ): CT Suitability
T1 | Core2 |  | 2500 | 1 | 120 | 6 | = =: 0.5FS5; #VALUE! x ( (: 10; #VALUE! +: 7.5; #VALUE! ) / (: -; #VALUE! +: XC-RACK POINTER; #VALUE! ): Suitable Dimensions
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )

## 5 (4) (hidden)
33kV Bus Bar (All Feeders)
Back to
INDEX

## IFP2 P545 (3) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | Line Protection(400kV FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core2 |  | Main-2 |  | (Differential + Distance) | [10 empty] | Connected devices: | P545
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-A
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 3750 |  | V | [12 empty] | Highest Vk required = | 2896.048
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P545 |  |  |  | Sr' | = | 0.02 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | Sl | = | 1.077 |  | VA
| Resisitance of the relay: | [10 empty] | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.02 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.02; Resisitance of the relay: Ir: W |  |  |  |  | = | 1.077 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, 2Rl |  |  | = | 0.02 |  | + | 1.077 |  | = | 1.097 |  | W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The knee point voltage of the CTs should comply with the minimum requirements of the formulae shown below:
| Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | ) | [9 empty] | …1
A constant depending on the maximum value of through fault current, If (as a multiple of In) and the primary system X/R ratio. K is determined as follows:
1 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 150% (k2 typically set at 150% for two-ended current differential schemes):
| When | ( | if |  | x | X/R | ) | ≤ | ( | 1000 | x | In | ) | [6 empty] | ...cond.1
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.07 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 1000 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 2600 | x | In | ) | …cond.2
| K | = | 107
2 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 100% (k2 typically set at 100% for tapped lines)
| When | ( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [6 empty] | ...cond.3
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) | …cond.4
| K | = | 256
| Resisitance of the relay: Rr: Maximum through fault current | [7 empty] | If |  | = | 50000 |  | A
| Resisitance of the relay: Rr: CT Primary Current | [7 empty] | Ipn |  | = | 2500 |  | A
| Resisitance of the relay: Rr: Maximum through fault current (referred to secondary) | [7 empty] | if |  | = | 20 |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [7 empty] | Rct |  | = | 5 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [7 empty] | 2Rl |  | = | 1.097 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [7 empty] | In |  | = | 1 |  | A
| Resisitance of the relay: Rr: Primary X/R ratio | [7 empty] | X/R |  | = | 40
| Resisitance of the relay: Rr: Enter the setting K2: | [10 empty] | 100 |  | %
| Checking condition |  |  |  | 3 & 4
( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [8 empty] | …cond.3
( | 20 |  | x | 40 | ) | ≤ | ( | 600 | x | 1 | )
| Resisitance of the relay: Sr': 800; Resisitance of the relay: x: ≤; Resisitance of the relay: ): 600 | [9 empty] | … | FALSE
| If | …cond.3 |  | is TRUE, the value of K must be highest of:
|  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | ) |  | Hence K |  | = | 320
|  |  | ≥ | 40 | + | 0.35 | x ( | 20 |  | x | 40 | )
|  |  | ≥ | 320
| OR | K | = | 65
( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) |  |  | …cond.4
( | 600 | x | 1 | ) | < | ( | 20 |  | x | 40 | ) | ≤ | ( | 1600 | x | 1 | )
| Resisitance of the relay: =: 600; Resisitance of the relay: Ir: <; Resisitance of the relay: ): 800 |  |  |  | ≤ |  | 1600 |  |  |  | … | TRUE
| Resisitance of the relay: Rr: If; Resisitance of the relay: =: …cond.4; Resisitance of the relay: / (: is TRUE, the value of K | = | 256 |  |  | Hence, final value of K |  |  |  |  | = | 256
Hence, Vk required for Diff. function:
|  |  | Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | )
|  |  |  | ≥ | 256 | x | 1 | x ( | 5 | + | 1.097 | )
|  |  |  | ≥ | 1560.8377 |  | V
|  | Available Vk |  |  | > | Required Vk
|  |  | 3750 |  | > | 1560.8377
|  |  |  | Hence CT is: |  | Suitably Dimensioned
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
For Close-in faults:
The calculation must be performed for all cables and lines where the source impedance ratio (SIR) may be less than SIR = 2.
| Resisitance of the relay: Ir: SIR; Resisitance of the relay: x: =; Resisitance of the relay: Ir: 27.7826 |  | Since SIR is >2, the below calculation is not applicable
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: x: Kmax; Resisitance of the relay: ): = | Fixed Dimentioning Factory = always 1.4 | [8 empty] | = | 1.4
| Resisitance of the relay: x: Ifmax; Resisitance of the relay: ): = | Max secondary phase-fault current | [8 empty] | = | 20 |  | A
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 1.4 | x | 20 |  | x | ( | 5 | + | 1.097 | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 170.7166 | Volts
Zone-1 reach point accuracy (RPA):
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: Sr': KRPA; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Fixed Dimentioning Factory = always 0.6 | [9 empty] | = | 0.6
| Resisitance of the relay: Sr': IFZ1; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Max secondary phase-fault current at Zone 1 reach point | [9 empty] | = | 19.3087 |  | A
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
|  | Vk | ≥ | 0.6 |  | x | 19.3087 |  | x ( | 1 | + | 40 | ) x ( | 5 | + | 1.097 | )
|  | Vk | ≥ | 2896.048 |  | Volts
| Resisitance of the relay: Rr: Hence, highest Vk required for Diff. & Dist. Functions: |  |  |  | 2896.048 |  | Volts
|  | Available Vk |  |  | > | Required Vk
|  |  | 3750 |  | > | 2896.048
|  |  |  | Hence CT is: |  | Suitably Dimensioned
Summary of CT parameters and its suitability
CT / Core | Resisitance of the relay: Sr': Ratio (A); Resisitance of the relay: x: CT Cable m/mm2; Resisitance of the relay: ): Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) |  | Connected Devices |  | CT Suitability
T1 | Core2 |  | 2500 |  | 1 | 120 | 6 | PX-A |  | 5 |  | 3750 |  | 60 |  | P545 |  | Suitably Dimensioned
[10 empty] | - |  | - |  | - |  |  |  | - | bar: Resisitance of the relay: Sr'
[10 empty] | - |  | - |  | - |  |  |  | - | bar: Resisitance of the relay: Sr'

## BUP BCU(3) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AK | Checked By |  |  | LN | Line Protection(400kV FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core3 | [14 empty] | Connected devices: | REF650
REC670
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | IDM+9
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | 5P20
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> |  |  | V | [12 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA
| Burden of |  | IDM+9 |  |  |  |  | = | 0.058 |  | VA |  | PE | = | In | x | In | x | Rct
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead + other burden | [5 empty] | PL | = | 1.175 |  | VA |  |  | = | 5 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula: | [21 empty] | The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2500 |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 0 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 5 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN | = | 30
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | 0 |  | x | 1 | ) / | 20 | ) - | 5
|  |  | = | -5 |  | VA
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 50000 |  | / | 2500
[5 empty] | = | 20
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 5 | + | 30 | ) / ( | 5 | + | 1.175 | )
[5 empty] | = | 113.3599
|  |  |  | Available Kssc' | = =: >; 20 n: Required Kssc'
|  |  | 113.3599 |  | = =: >; 20 n: 20
|  |  |  | Hence CT is: | 20 n: Suitably Dimentioned
| T1 |  | Core3 |  | 20 x ( (: 0 |  |  | Connected devices: | REF650
| 0 | [17 empty] | REC670
[5 empty] | 20 x ( (: Tap-1; 20 +: Tap-2; 20 ) / (: Tap-3 |  |  |  | IDM+9
| CT Ratio: |  |  |  | 20 x ( (: 2500; 20 +: -; 20 ) / (: -; 20 +: /; 20 PL: 1; 20 ): A
| Class of Accuracy: |  |  |  | 20 +: 5P20
| CT Resistance: |  |  |  | 20 PE: Rct<; 20 +: -; 20 ) / (: W
| Knee Point Voltage: |  |  |  | 20 PE: Vk>; 20 +: -; 20 ) / (: V | [6 empty] | #VALUE!
| Magnetizing Current: |  |  |  | 20 PE: I0<; 20 +: -; 20 ) / (: mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  | 20 PE: =; 20 +: 0.02; 20 ) / (: VA; 20 +: CT internal Burden
| Burden of |  | REC670 |  | 20 PE: =; 20 +: 0.02; 20 ) / (: VA
| Burden of |  | IDM+9 |  | 20 PE: =; 20 +: 0.058; 20 ) / (: VA; 20 +: PE; 20 PL: =; 20 ): In | x | In | x | Rct
| Total lead burden |  |  |  | 20 PE: =; 20 +: 1.077; 20 ) / (: VA; 20 PL: =; 20 ): 1 | x | 1 | x | -
| Total lead + other burden |  |  |  | 20 x ( (: PL; 20 PE: =; 20 +: 1.175; 20 ) / (: VA; 20 PL: =; 20 ): #VALUE! |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | - |  | V
|  | Internal Burden, | [13 empty] | PE | = | #VALUE! |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | - |  | x | 1 | ) / | 20 | ) - | #VALUE!
|  |  | = | #VALUE! | bar: 20 n
ABB
|  |  |  | Required Kssc' | = =: =; 20 n: Itkmax; 20 PE: /; 20 +: Ipn
[5 empty] | = | 50000 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | #VALUE! | + | #VALUE! | ) / ( | #VALUE! | + | 1.175 | )
[5 empty] | = | #VALUE!
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | #VALUE! |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
ABB
| T1 |  | Core3 |  | #VALUE! x ( (: 0 |  |  | Connected devices: | REF650
| 0 | [17 empty] | REC670
[5 empty] | #VALUE! x ( (: Tap-1; #VALUE! +: Tap-2; #VALUE! ) / (: Tap-3 |  |  |  | IDM+9
| CT Ratio: |  |  |  | #VALUE! x ( (: 2500; #VALUE! +: -; #VALUE! ) / (: -; #VALUE! +: /; #VALUE! PL: 1; #VALUE! ): A
| Class of Accuracy: |  |  |  | #VALUE! ) / (: 5P20
| CT Resistance: |  |  |  | #VALUE! PN: Rct<; #VALUE! ) / (: -; #VALUE! +: W
| Knee Point Voltage: |  |  |  | #VALUE! PN: Vk>; #VALUE! ) / (: -; #VALUE! +: V | [6 empty] | #VALUE!
| Magnetizing Current: |  |  |  | #VALUE! PN: I0<; #VALUE! ) / (: -; #VALUE! +: mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA; #VALUE! +: CT internal Burden
| Burden of |  | REC670 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA
| Burden of |  | IDM+9 |  | #VALUE! PE: =; #VALUE! +: 0.058; #VALUE! ) / (: VA; #VALUE! +: PE; #VALUE! PL: =; #VALUE! ): In | x | In | x | Rct
| Total lead burden |  |  |  | #VALUE! PE: =; #VALUE! +: 1.077; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): 1 | x | 1 | x | -
| Total lead + other burden |  |  |  | #VALUE! x ( (: PL; #VALUE! PE: =; #VALUE! +: 1.175; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): #VALUE! |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | - |  | V
|  | Internal Burden, | [13 empty] | PE | = | #VALUE! |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | - |  | x | 1 | ) / | 20 | ) - | #VALUE!
|  |  | = | #VALUE! | bar: #VALUE! n
ABB
|  |  |  | Required Kssc' | = =: =; #VALUE! n: Itkmax; #VALUE! PE: /; #VALUE! +: Ipn
[5 empty] | = | 50000 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | #VALUE! | + | #VALUE! | ) / ( | #VALUE! | + | 1.175 | )
[5 empty] | = | #VALUE!
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | #VALUE! |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | #VALUE! n: CT Cable m/mm2; #VALUE! PE: Class; #VALUE! PN: CT Resistance (W) @ 75OC; #VALUE! PE: Rated Vk (V); #VALUE! PL: Im @ Vk (mA) | Connected Devices |  | CT Suitability
T1 | Core3 |  | 2500 |  | 1 | 120 | 6 | 5P20 | #REF! | 5 |  | - |  | - |  | REF650 REC670 IDM+9 |  | Suitably Dimentioned
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL

## GIB - REF650 (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AK | Checked By |  |  | LN | Line Protection(400kV FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core4 | [14 empty] | Connected devices: | REF650
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [11 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Total lead burden | [6 empty] | = | 2.7035 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead + other burden | [5 empty] | PL | = | 2.7235 |  | VA |  |  | = | 5 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2500 |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 750 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 5 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 2.7235 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN | = | 43.75
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | 750 |  | x | 1 | ) / | 20 | ) - | 5
|  |  | = | 43.75 |  | VA
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 50000 |  | / | 2500
[5 empty] | = | 20
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 5 | + | 43.75 | ) / ( | 5 | + | 2.7235 | )
[5 empty] | = | 126.2381
|  |  |  | Available Kssc' | = =: >; 20 n: Required Kssc'
|  |  | 126.2381 |  | = =: >; 20 n: 20
|  |  |  | Hence CT is: | 20 n: Suitably Dimentioned
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | 20 n: CT Cable m/mm2; 20 PE: Class; 20 PN: Rct @ 75OC (Ω); 20 PE: Rated Vk (V); 20 PL: Im @ Vk (mA) | Connected Devices |  | CT Suitability
T1 | Core4 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 |  | REF650 |  | Suitably Dimentioned
|  |  | - | [14 empty] | - | bar: 20 PN; 20 PE; 20 PL
|  |  | - | [14 empty] | - | bar: 20 PN; 20 PE; 20 PL

## BBP FU1 - REB500 (3) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | Line Protection(400kV FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
I
| T1 |  | Core5 | [14 empty] | Connected devices: | REB500
P743
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  |  |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [12 empty] | #REF!
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 5 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.187 |  | VA
CT-Requirements for BB Protection
|  | Maximum Primary Fault Current | [13 empty] | Isc | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2500 |  | A
|  | Rated Voltage | [13 empty] | UN2 | = | 400 |  | kV
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 750 |  | V
|  | Internal Resistance CT | [13 empty] | Rct | = | 5 |  | VA
|  | Conn. Lead + Relay Burden | [13 empty] | RL | = | 1.187 |  | VA
|  | Rated Secondary Current, | [13 empty] | Isc | = | 1 |  | A
|  | Nominal Frequency of the network | [13 empty] | fn | = | 50
Required OC factor condition. 1:
At Max. Through fault current CT’s shall not saturate for currents below 5 times rated current.
[8 empty] | n' | = | Isc
5 * Ipn
Required OC factor Condition 2:
n2' >= 10 for TN <=120 msec
n2' >= 20 for 120ms <= TN <=300 ms
| Where, |  | n' = Required OC factor
Isc = max. bus fault current
Ipn = Rated primary current (A)
Required OC factor condition 1:
|  | n'(1) | = | 50000
5 x 2500
|  | n'(1) | = | 4
Required OC factor condition 2:
|  |  |  | TN = | 1 |  | X | X
[6 empty] | 2* ϖ* fn |  | R
[5 empty] | 1 |  |  |  | x | 15
|  |  | TN | = | 2 * 3.14 * 50
|  |  |  | = | 0.047771 |  | sec
|  |  | TN | = | 47.7707 |  | ms
| Hence n'(2) 10 |  |  | = | 10
Required OC factor n' >= max( n'(1) ; n'(2))
n' >=max(4 ; 10)
Therefore
|  | n' | = | 10 |  | Necessary Condition
Required secondary equivalent limiting secondary e.m.f
Eal >= n' *(RCT+RL+Rr)*Isn
| = | 10 | x | ( | 5 |  | + | 1.187 | + | 0.01 | ) | x | 1
| Eal | = | 61.9702 | V
| According to IEC 61869 class PX | [7 empty] | Eknee |  | > |  | 0.8*Eal
[11 empty] | = |  | 49.5762
[5 empty] | With design margin 120% | [5 empty] | = |  | 59.4914
[10 empty] | Available Vk | > | Required Vk
[8 empty] | 750 |  |  | > | 59.4914
[10 empty] | Hence CT is: |  | Suitable Dimensions
| T1 |  | Core5 |  |  |  | 0 | [10 empty] | Connected devices: | REB500
[19 empty] | P743 |  |  | Required Vk
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | 0 |  | - |  | / | 1 | A
| Class of Accuracy: | [7 empty] | PX-B
| CT Resistance: | [6 empty] | Rct< | 9.3 |  | W
| Knee Point Voltage: | [6 empty] | Vk> | 500 |  | V
| Magnetizing Current: | [6 empty] | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 9.3
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 9.3 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.187 |  | VA
CT-Requirements for BB Protection
|  | Maximum Primary Fault Current | [13 empty] | Isc | = | 31500 |  | A | **
|  | CT Primary Current, | [13 empty] | Ipn | = | 0 |  | A
|  | Rated Voltage | [13 empty] | UN2 | = | 33 |  | kV
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 500 |  | V
|  | Internal Resistance CT | [13 empty] | Rct | = | 9.3 |  | VA
|  | Conn. Lead + Relay Burden | [13 empty] | RL | = | 1.187 |  | VA
|  | Rated Secondary Current, | [13 empty] | Isc | = | 1 |  | A
|  | Nominal Frequency of the network | [13 empty] | fn | = | 50
Required OC factor condition. 1:
At Max. Through fault current CT’s shall not saturate for currents below 5 times rated current.
[8 empty] | n' | = | Isc
5 * Ipn
Required OC factor Condition 2:
n2' >= 10 for TN <=120 msec
n2' >= 20 for 120ms <= TN <=300 ms
Where,
n' = Required OC factor
Isc = max. bus fault current
Ipn = Rated primary current (A)
[10 empty] | ** | Rated Bus fault current
Required OC factor condition 1:
|  | n'(1) | = | 31500
5 x 0
|  | n'(1) | = | #DIV/0!
Required OC factor condition 2:
|  |  |  | TN = | 1 |  | X | X
[6 empty] | 2* ϖ* fn |  | R
| As per Transco Standard for 33kV system X/R | [11 empty] | = | #REF!
[5 empty] | 1 |  |  |  | x | #REF!
|  |  | TN | = | 2 * 3.14 * 50
|  |  |  | = | #REF! |  | sec
|  |  | TN | = | #REF! |  | ms
| Hence n'(2) 10 |  |  | = | 10
Required OC factor n' >= max( n'(1) ; n'(2))
n' >=max(3.15 ; 10)
Therefore
|  | n' | = | #DIV/0! |  | Necessary Condition
Required secondary equivalent limiting secondary e.m.f
Eal >= n' *(RCT+RL+Rr)*Isn
| = | #DIV/0! | x | ( | 9.3 |  | + | 1.187 | + | 0.01 | ) | x | 1
| Eal | = | #DIV/0! | V
| According to IEC 61869 class PX | [7 empty] | Eknee |  | > |  | 0.8*Eal
[11 empty] | = |  | #DIV/0!
[5 empty] | With design margin 120% | [5 empty] | = |  | #DIV/0!
[10 empty] | Available Vk | #DIV/0! | Required Vk
[9 empty] | 500 |  | #DIV/0! | #DIV/0!
[10 empty] | Hence CT is: |  | #DIV/0!
| T1 |  | Core5 |  |  |  | 0 | [10 empty] | Connected devices: | REB500
[19 empty] | P743 |  |  | #VALUE!
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | 0 |  | - |  | / | 1 | A
| Class of Accuracy: | [9 empty] | PX-B
| CT Resistance: | [8 empty] | Rct< | - |  | W
| Knee Point Voltage: | [8 empty] | Vk> | - |  | V
| Magnetizing Current: | [8 empty] | I0< | - |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | #VALUE! |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.187 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 1 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | - |  | V
|  | Internal Burden, | [13 empty] | PE | = | #VALUE! |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.187 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | - |  | x | 1 | ) / | 20 | ) - | #VALUE!
|  |  | = | #VALUE! |  | VA
The CT requirement is as follows:
where
| n' | ³ | n1 |  | --- (i) |  |  |  |  | n' | = | The effective accuracy limiting factor
| n' | ³ | n2 |  | --- (ii) | [5 empty] | = | n x (PN + PE) / (PL + PE)
[10 empty] | n1 | = | Itkmax / (5 x Ipn)
[10 empty] | n2 | = | 10 |  | ...for | TP | £ | 120 | msec
[11 empty] | = | 20 |  | ...for | TP | £ | 300 | msec
Calculation for n1: | [9 empty] | n1 | = | Itmax |  | / ( | 5 | x | Ipn |  | )
[11 empty] | = | 1 |  | / ( | 5 | x | - |  | )
[11 empty] | = | #VALUE!
Calculation for n2: |  |  |  | Since Tp |  | = | #REF! |  | , | n2 | = | #REF!
Calculation for n': | [5 empty] | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[6 empty] | = | 20 | x ( ( | #VALUE! | + | #VALUE! | ) / ( | #VALUE! | + | 1.187 | )
[6 empty] | = | #VALUE!
Checking the conditions ---(i) and ---(ii) mentioned aove:
|  |  | #VALUE! |  | #VALUE! | =: #VALUE!; PE: --- (i)
|  |  | #VALUE! |  | #VALUE! | =: #REF!; PE: --- (ii)
|  |  |  | Hence CT is: |  | =: #VALUE!
CT-Requirements for BB Protection (P743)
|  | CT Primary Current, |  |  |  | ): Ipn | = | 2500 |  | A
|  | Max primary fault current (same for all feeders) |  |  |  | ): IFmax | = | 50000 |  | A
|  | Max secondary fault current (same for all feeders) |  |  |  | ): Ifmax | = | 20 |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices |  |  |  | ): Rb' | = | 1.187 |  | W
|  | Max primary contribution from a feeder to an internal fault |  |  |  | ): IFmax int | = | 50000 |  | A
|  | Max secondary contribution from a feeder to an internal fault |  |  |  | ): Ifmax int | = | 20 |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | =: Ifmax; x ( (: x (; PE: Rct; PN: +; ) / (: Rb'; +: )
|  |  | = | 0.5 | x | =: 20; x ( (: x (; PE: 5; PN: +; ) / (: 1.187; +: )
|  |  | = | 61.8702
Criteria II
| Vk |  | >= | Ifmax int |  | =: x (; n: Rct; PE: +; +: Rb'; ) / (: )
|  |  | = | 20 |  | =: x (; n: 5; PE: +; +: 1.187; ) / (: )
|  |  | = | 123.7404
Adequacy Check
Criteria I
[5 empty] | Available Vk | =: >; n: Required Vk; PN: (Criteria I)
|  |  |  | 750 |  | =: >; n: 61.8702
[5 empty] | Hence: | n: Criteria I; PE: is; +: Satisfied
Criteria II
[5 empty] | Available Vk | =: >; n: Required Vk; PN: (Criteria II)
|  |  |  | 750 |  | =: >; n: 123.7404
[5 empty] | Hence: | n: Criteria II; PE: is; +: Satisfied
[5 empty] | Hence CT is: | n: Suitably Dimentioned
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | =: CT Cable m/mm2; x ( (: Class; +: CT Resistance (W) @ 75OC; ) / (: Limiting Secondary Voltage (Ual), V; +: Mag. Current (Io), mA at Vk; ): Relay / Instrument Type |  | CT Suitability
T1 | Core5 |  | 2500 |  | 1 | 120 | 6 | PX-B | #REF! | 5 |  | 750 |  | 60 |  | REB500 P743 |  | Suitable Dimensions
|  |  | 0 | [14 empty] | Suitably Dimentioned | bar: +; ) / (; +
|  |  | - | [14 empty] | - | bar: +; ) / (; +

## P74X-X (3) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2025-09-25
[7 empty] | 33kV DF5W SS | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV CABLE FEEDERS | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core5 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | P743
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 1500 | [5 empty] | / | 1 | A
| Class of Accuracy: | [5 empty] | X
| CT Resistance: |  |  |  |  | Rct< | 6 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 500 |  | V | [12 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< | 10 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Total lead burden | [6 empty] | = | 0.56186 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 0.66186 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 55677 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 1500 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | 37.118 |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 0.66186 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 30000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | 20 |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | 37.118 |  | x ( | 6 |  | + | 0.66186 |  | )
|  |  | = | 123.6375
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 20 |  | x ( | 6 |  | + | 0.66186 |  | )
|  |  | = | 133.2372
Adequacy Check
Criteria I
[5 empty] | Available Vk | > | Required Vk |  |  |  | (Criteria I)
|  |  |  | 500 |  | > | 123.6375
[5 empty] | Hence: |  | Criteria I |  | is | Satisfied
Criteria II
[5 empty] | Available Vk | > | Required Vk |  |  |  | (Criteria II)
|  |  |  | 500 |  | > | 133.2372
[5 empty] | Hence: |  | Criteria II |  | is | Satisfied
[5 empty] | Hence CT is: |  | Suitably Dimentioned
| T1 |  | Core5 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | P743
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 1500 |  | 0 |  | 0 |  | / | 1 | A
| Class of Accuracy: | [7 empty] | X
| CT Resistance: | [6 empty] | Rct< |  |  | W
| Knee Point Voltage: | [6 empty] | Vk> |  |  | V | [10 empty] | Under Dimentioned
| Magnetizing Current: | [6 empty] | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Total lead burden | [6 empty] | = | 0.56186 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 0.66186 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 55677 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 1500 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | 37.118 |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 0.66186 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 30000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | 20 |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | 37.118 |  | x ( | 0 |  | + | 0.66186 |  | )
|  |  | = | 12.2835
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 20 |  | x ( | 0 |  | + | 0.66186 |  | )
|  |  | = | 13.2372
Adequacy Check
Criteria I
[5 empty] | Available Vk | < | Required Vk |  |  |  | (Criteria I)
|  |  |  | 0 |  | < | 12.2835
[5 empty] | Hence: |  | Criteria I |  | is | Not Satisfied
Criteria II
[5 empty] | Available Vk | < | Required Vk |  |  |  | (Criteria II)
|  |  |  | 0 |  | < | 13.2372
[5 empty] | Hence: |  | Criteria II |  | is | Not Satisfied
[5 empty] | Hence CT is: |  | Under Dimentioned
ABB
| T1 |  | Core5 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | P743
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 1500 |  | 0 |  | 0 |  | / | 1 | A
| Class of Accuracy: | [9 empty] | X
| CT Resistance: | [8 empty] | Rct< |  |  | W
| Knee Point Voltage: | [8 empty] | Vk> |  |  | V | [8 empty] | #DIV/0!
| Magnetizing Current: | [8 empty] | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Total lead burden | [6 empty] | = | 0.56186 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 0.66186 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 55677 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 0 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | #DIV/0! |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 0.66186 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 30000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | #DIV/0! |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | #DIV/0! |  | x ( | 0 |  | + | 0.66186 |  | )
|  |  | = | #DIV/0!
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | #DIV/0! |  | x ( | 0 |  | + | 0.66186 |  | )
|  |  | = | #DIV/0!
ABB
Adequacy Check
Criteria I
[5 empty] | Available Vk | #DIV/0! | Required Vk |  |  |  | (Criteria I)
|  |  |  | 0 |  | #DIV/0! | #DIV/0!
[5 empty] | Hence: |  | Criteria I |  | is | #DIV/0!
Criteria II
[5 empty] | Available Vk | #DIV/0! | Required Vk |  |  |  | (Criteria II)
|  |  |  | 0 |  | #DIV/0! | #DIV/0!
[5 empty] | Hence: |  | Criteria II |  | is | #DIV/0!
[5 empty] | Hence CT is: |  | #DIV/0!
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  |  |  | CT Cable m/mm2 |  | Class |  | CT Resistance (W) @ 75OC |  | CT Resistance (W) @ 75OC | Knee point Voltage (Vk), V |  |  | Mag. Current (Io), mA at Vk |  |  | Relay / Instrument Type
T1 |  | Core5 | 1500 | 0 | 0 | 1 | 75 | 6 | X |  | 6 | 0 | 0 | 500 | 0 | 0 | 10 | 0 | 0 | P743
0
0

## COP MAIN (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | Line Protection(400kV FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core6 |  |  | (Metering Main) | [10 empty] | Connected devices: | XC-RACK
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.2S
| CT Resistance: |  |  |  | Rct< | 5 |  | W
| Factor of Safety |  |  |  | FS | 5 | [13 empty] | Suitable Dimensions
| Rated Burden |  |  |  | PN | 10 |  | VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [9 empty] | rec670 | 100A for 1 S
| Burden of |  | 0 |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 5 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 1.085 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 2500 |  | A
| Internal Burden, | [10 empty] | PE | = | 5 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 1.085 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | Pn | = | 5
| Safety Factor Fs (min) | [11 empty] | = | 20 | [6 empty] | Safety Factor among all connected devices Fs (min)
XC-RACK = 20 A for 0.5 sec Refer annuxure mail received from manufacturer
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 1.085
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 5 | x ( ( | 5 | + | 10 | ) / ( | 5 | + | 1.085 | )
[7 empty] | = | 12.3253
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.085 FS: Total Connected Burden; 1.085 ): …cond.1
[5 empty] | 10 |  | = =: >; 1.085 FS: 1.085; 1.085 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.085 FS: Effective Safety Factor of CT, FS'; 1.085 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.085 FS: 12.3253; 1.085 ): Satisfied
[6 empty] | Hence CT is: | 1.085 FS: Suitable Dimensions
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; 1.085 x ( (: CT Resistance (W) @ 75OC; 1.085 +: Rated Burden VA; 1.085 +: Relay / Instrument Type; 1.085 ): CT Suitability
T1 | Core6 |  | 2500 | 1 | 120 | 6 | = =: 0.2S; 1.085 x ( (: 5; 1.085 +: 10; 1.085 ) / (: -; 1.085 +: XC-RACK; 1.085 ): Suitable Dimensions
- | bar: 1.085 x ( (; 1.085 +; 1.085 ) / (; 1.085 )
- | bar: 1.085 x ( (; 1.085 +; 1.085 ) / (; 1.085 )

## COP CHECK (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | Line Protection(400kV FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core7 |  |  | (Metering Check) | [10 empty] | Connected devices: | XC-RACK
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 2000 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.2S
| CT Resistance: |  |  |  | Rct< | 5 |  | W
| Factor of Safety |  |  |  | FS | 5 | [13 empty] | Suitable Dimensions
| Rated Burden |  |  |  | PN | 10 |  | VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [9 empty] | rec670 | 100A for 1 S
| Burden of |  | 0 |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 5 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 1.085 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 2000 |  | A
| Internal Burden, | [10 empty] | PE | = | 5 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 1.085 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | Pn | = | 5
| Safety Factor Fs (min) | [11 empty] | = | 20 | [6 empty] | Safety Factor among all connected devices Fs (min)
XC-RACK = 20 A for 0.5 sec Refer annuxure mail received from manufacturer
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 1.085
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 5 | x ( ( | 5 | + | 10 | ) / ( | 5 | + | 1.085 | )
[7 empty] | = | 12.3253
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.085 FS: Total Connected Burden; 1.085 ): …cond.1
[5 empty] | 10 |  | = =: >; 1.085 FS: 1.085; 1.085 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.085 FS: Effective Safety Factor of CT, FS'; 1.085 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.085 FS: 12.3253; 1.085 ): Satisfied
[6 empty] | Hence CT is: | 1.085 FS: Suitable Dimensions
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; 1.085 x ( (: CT Resistance (W) @ 75OC; 1.085 +: Rated Burden VA; 1.085 +: Relay / Instrument Type; 1.085 ): CT Suitability
T1 | Core7 |  | 2000 | 1 | 120 | 6 | = =: 0.2S; 1.085 x ( (: 5; 1.085 +: 10; 1.085 ) / (: -; 1.085 +: XC-RACK; 1.085 ): Suitable Dimensions
- | bar: 1.085 x ( (; 1.085 +; 1.085 ) / (; 1.085 )
- | bar: 1.085 x ( (; 1.085 +; 1.085 ) / (; 1.085 )

## GIB - REF650 (2) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AK | Checked By |  |  | LN | Line Protection(400kV FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core4 | [14 empty] | Connected devices: | REF650
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [11 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Total lead burden | [6 empty] | = | 2.7035 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead + other burden | [5 empty] | PL | = | 2.7235 |  | VA |  |  | = | 5 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2500 |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 750 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 5 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 2.7235 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN | = | 43.75
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | 750 |  | x | 1 | ) / | 20 | ) - | 5
|  |  | = | 43.75 |  | VA
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 50000 |  | / | 2500
[5 empty] | = | 20
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 5 | + | 43.75 | ) / ( | 5 | + | 2.7235 | )
[5 empty] | = | 126.2381
|  |  |  | Available Kssc' | = =: >; 20 n: Required Kssc'
|  |  | 126.2381 |  | = =: >; 20 n: 20
|  |  |  | Hence CT is: | 20 n: Suitably Dimentioned
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | 20 n: CT Cable m/mm2; 20 PE: Class; 20 PN: Rct @ 75OC (Ω); 20 PE: Rated Vk (V); 20 PL: Im @ Vk (mA) | Connected Devices |  | CT Suitability
T1 | Core4 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 |  | REF650 |  | Suitably Dimentioned
|  |  | - | [14 empty] | - | bar: 20 PN; 20 PE; 20 PL
|  |  | - | [14 empty] | - | bar: 20 PN; 20 PE; 20 PL

## BAY4 (hidden)
Line Protection HVDC FEEDERS BC3 (09, 05, 03 ,02, 04, 08)
Back to
INDEX

## IFP1-RED670 (2) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | Line Protection(HVDC FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core1 |  |  |  | (Diff. + Dist.) | [10 empty] | Connected devices: | RED670 |  | Note: CT requirements for other protection functions are different. Pl. refer to Application Manual
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-A
| CT Resistance: |  |  |  |  | Rct < | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk > | 3750 |  | V | [11 empty] | Highest Vk required = |  | 285.3205
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | RED670 |  |  |  | Sr' | = | 0.02 |  | VA |  | Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Burden of | [6 empty] | = |  |  | VA |  |  | = | 1.097 | / ( | 1 | x | 1 | )
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  | Lead + Other resisitance connected =: =; Lead + Other resisitance connected Sl: 1.097; Lead + Other resisitance connected Isn: W
| Total lead + other burden | [5 empty] | Sl | = | 1.097 |  | VA
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer.
For Close-in faults:
Ealreq = |  |  |  |  | Ikmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
For Through faults:
Ealreq = |  |  | 2 | x | Itmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
| Equivalent Secondary emf. Required | [11 empty] | Lead + Other resisitance connected Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Lead + Other resisitance connected Sl: Ipn; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 2500; Lead + Other resisitance connected Isn: A
| Max. primary fundamental frequency fault current for close-in faults | [11 empty] | Lead + Other resisitance connected Sl: Ikmax; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 50000; Lead + Other resisitance connected Isn: A
| Max. primary fundamental frequency fault current for through fault | [13 empty] | Itmax | = | 47858.0776 |  | A | 3-phase
[16 empty] | = | 48245.339 |  | A | 1-phase
| CT secondary rated current | [11 empty] | Lead + Other resisitance connected Sl: Isn; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 1; Lead + Other resisitance connected Isn: A
| Relay rated current | [11 empty] | Lead + Other resisitance connected Sl: Ir; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 1; Lead + Other resisitance connected Isn: A
| CT secondary winding resistance. | [11 empty] | Lead + Other resisitance connected Sl: Rct; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 5; Lead + Other resisitance connected Isn: W
| Lead Resistance of the current loop from the CT to Relay | [11 empty] | Lead + Other resisitance connected Sl: Rl; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 1.097; Lead + Other resisitance connected Isn: W
| Burden of RED 670 Relay | [11 empty] | Lead + Other resisitance connected Sl: Sr; Lead + Other resisitance connected / (: =; Lead + Other resisitance connected Isn: 0.02; Lead + Other resisitance connected Isn: VA
For Close-in faults:
Ealreq = |  |  |  |  | 50000 |  | x | 1 |  | x | ( | 5 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
2500 | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
|  | = | 122.3404 |  | V
For Through faults (3-ph):
Ealreq = |  |  | 2 | x | 47858.0776 |  | x | 1 |  | x | ( | 5 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
2500 | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
|  | = | 234.1991 |  | V
For Through faults (1-ph):
Ealreq = |  |  | 2 | x | 48245.339 |  | x | 1 |  | x | ( | 5 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
2500 | bar: Lead + Other resisitance connected / ( to Lead + Other resisitance connected x
|  | = | 236.0943 |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer.
For Close-in faults:
Ealreq = |  |  | Ikmax |  | x | Isn |  | x | a | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
For Endzone-1 faults:
Ealreq = |  |  | Ikzone-1 |  | x | Isn |  | x | k | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipn; Sr: = | 2500 |  | A
| Max. primary fundamental frequency fault current for close-in faults | [6 empty] | +: Ikmax; Sr: = | 50000 |  | A
| Max. primary fundamental frequency fault current for zone-1 faults | [6 empty] | +: Ikzone-1; Sr: = | 48271.7306 |  | A | 3-phase
[17 empty] | 48587.1707 |  | A | 1-phase | bar: Sr
| CT secondary rated current . | [6 empty] | +: Isn; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | 5 |  | W
| Lead resistance between relay and CT sec. Terminals (2 way ) | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of RED 670 Relay | [15 empty] | 0.02 |  | VA | bar: + to Sr
High Speed Distance : Quadrilateral Characteristic
Factor for the Function of the primary time constant for the DC component in the fault current
[7 empty] | For the primary time constant tp | x: <= 400ms; x: :; (: a; +: =; Sr: 1
Factor for Function of the primary time constant for the DC component in the fault current
for a three phase fault at the set reach component in the fault current for of zone-1
[7 empty] | For the primary time constant tp | x: <= 200ms; x: :; (: k; +: =; Sr: 3
For Close-in faults:
[6 empty] | Since System tp |  |  |  | = | 127.2727 |  | ms, | a | = | 1
Ealreq = |  |  | 50000 |  | x | 1 |  | x | 1 | x | ( | 5 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
[6 empty] | 2500 | [10 empty] | x | 1 | bar: Sr
|  | = | 122.3404 |  | V
For Endzone-1 3-ph faults:
|  |  |  | Since 3-ph tp for this fault | [5 empty] | = | 111.098 |  | ms, | k | = | 3
Ealreq = |  |  | 48271.7306 |  | x | 1 |  | x | 3 | x | ( | 5 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | 2500 | [10 empty] | x | 1 | bar: Sr
|  | = | 354.3351 |  | V
For Endzone-1 1-ph faults:
|  |  |  | Since 1-ph tp for this fault | [5 empty] | = | 86.3428 |  | ms, | k | = | 3
Ealreq = |  |  | 48587.1707 |  | x | 1 |  | x | 3 | x | ( | 5 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | 2500 | [10 empty] | x | 1 | bar: Sr
|  | = | 356.6506 |  | V
Hence, highest Ealreq for Differential & Distance functions at | [7 empty] | Rct: 2500; Rl: A Tap =; Sr: 356.6506 |  | V
Therefore, the required knee point voltage of the CT.
(Vk in terms of Ealreq as per the Manufacturer )
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: 356.6506 |  | x | 0.8
[8 empty] | +: =; Sr: 285.3205 |  | V
|  |  | Available Vk |  |  | > | Required Vk | [14 empty] | >
|  |  |  | 3750 |  | > | 285.3205
[5 empty] | Hence CT is: |  | Suitably Dimensioned | [14 empty] | Suitably Dimensioned
C. CT ADEQUECY CHECK FOR BREAKER FAILURE FUNCTION:
The CTs must have a rated equivalent secondary e.m.f. Eal that is larger than the maximum of the required secondary em.f. Ealreq as per below equation (1) (Refer : Annexure-G)
Ealreq = |  |  | 5 | x | Iop |  | x | Isr |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[8 empty] | x: Ipr; Sr: Ir | x | Ir
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipr; Sr: = | 2500 |  | A
| Primary operate current | [6 empty] | +: Iop; Sr: = | 50000 |  | A
| CT secondary rated current | [6 empty] | +: Isr; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | 5 |  | W
| Total Lead Resistance | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of REQ 650 Relay | [15 empty] | 0 |  | VA | bar: + to Sr
| CT Iopernal Burden |  |  |  | PE = | Rct | x | x: Isr; k: x; x: Isr; +: PE; Sr: = | 5 |  | VA
| Rated CT Burden | [15 empty] | 285.3205 |  | VA | bar: + to Sr
| Rated ALF | [15 empty] | 0 | bar: + to Sr
Ealreq = |  |  | 5 | x | 50000 |  | x | 1 |  | x | ( | 5 | + | 1.097 | + | 0 |  |  | ) | ---(1)
[8 empty] | x: 2500; Sr: 1 | x | 1
|  | = | 609.7022 |  | V
Therefore, the required knee point voltage of the CT.
(Vk in terms of Ealreq as per the Manufacturer Refer Annexure-B)
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: 609.7022 |  | x | 0.8
[8 empty] | +: =; Sr: 487.7618 |  | V
|  |  | Available Vk |  |  | > | Required Vk
|  |  |  | 3750 |  | > | 487.7618
[5 empty] | Hence CT is: |  | Suitably Dimensioned
| T1 |  | Core1 |  | 0 |  | (Diff. + Dist.) | [10 empty] | Connected devices: | RED670
| 0 | [17 empty] | 0
[7 empty] | Tap-1 | k: Tap-2; (: Tap-3 |  |  | 0
| CT Ratio: | [5 empty] | 2500 | k: -; (: -; +: /; Rl: 1; +: A
| Class of Accuracy: | [6 empty] | k: PX-A
| CT Resistance: | [6 empty] | x: Rct<; k: 3; (: W
| Knee Point Voltage: | [6 empty] | x: Vk>; k: 200; (: V |  |  |  |  | Highest Vk required = |  | #VALUE!
| Magnetizing Current: | [6 empty] | x: I0<; k: 100; (: mA at Vk
Other Burdens on same CT core:
| Burden of |  | RED670 |  |  |  | Sr' | x: =; k: 0.02; (: VA; +: Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | x: =; k: 0; (: VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1.097 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.097 |  | VA |  | =: =; Sl: 1.097; Isn: W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer.
For Close-in faults:
Ealreq = |  |  |  |  | Ikmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
For Through faults:
Ealreq = |  |  | 2 | x | Itmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: -; Isn: A
| Max. primary fundamental frequency fault current for close-in faults | [11 empty] | Sl: Ikmax; / (: =; Isn: 50000; Isn: A
| Max. primary fundamental frequency fault current for through fault | [13 empty] | Itmax | = | 47858.0776 |  | A | 3-phase
[16 empty] | = | 48245.339 |  | A | 1-phase
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: 3; Isn: W
| Lead Resistance of the current loop from the CT to Relay | [11 empty] | Sl: Rl; / (: =; Isn: 1.097; Isn: W
| Burden of RED 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
For Close-in faults:
Ealreq = |  |  |  |  | 50000 |  | x | 1 |  | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
- | bar: / ( to x
|  | = | #VALUE! |  | V
For Through faults (3-ph):
Ealreq = |  |  | 2 | x | 47858.0776 |  | x | 1 |  | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
For Through faults (1-ph):
Ealreq = |  |  | 2 | x | 48245.339 |  | x | 1 |  | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer. Ref Annexure-B
For Close-in faults:
Ealreq = |  |  | Ikmax |  | x | Isn |  | x | a | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
For Endzone-1 faults:
Ealreq = |  |  | Ikzone-1 |  | x | Isn |  | x | k | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipn; Sr: = | - |  | A
| Max. primary fundamental frequency fault current for close-in faults | [6 empty] | +: Ikmax; Sr: = | 50000 |  | A
| Max. primary fundamental frequency fault current for zone-1 faults | [6 empty] | +: Ikzone-1; Sr: = | 48271.7306 |  | A | 3-phase
[17 empty] | 48587.1707 |  | A | 1-phase | bar: Sr
| CT secondary rated current . | [6 empty] | +: Isn; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | 3 |  | W
| Lead resistance between relay and CT sec. Terminals (2 way ) | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of RED 670 Relay | [15 empty] | 0.02 |  | VA | bar: + to Sr
High Speed Distance : Quadrilateral Characteristic
Factor for the Function of the primary time constant for the DC component in the fault current
[7 empty] | For the primary time constant tp | x: <= 400ms; x: :; (: a; +: =; Sr: 1
Factor for Function of the primary time constant for the DC component in the fault current
for a three phase fault at the set reach component in the fault current for of zone-1
[7 empty] | For the primary time constant tp | x: <= 200ms; x: :; (: k; +: =; Sr: 3
For Close-in faults:
[6 empty] | Since System tp |  |  |  | = | 127.2727 |  | ms, | a | = | 1
Ealreq = |  |  | 50000 |  | x | 1 |  | x | 1 | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
For Endzone-1 3-ph faults:
|  |  |  | Since 3-ph tp for this fault | [5 empty] | = | 111.098 |  | ms, | k | = | 3
Ealreq = |  |  | 48271.7306 |  | x | 1 |  | x | 3 | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
For Endzone-1 1-ph faults:
|  |  |  | Since 1-ph tp for this fault | [5 empty] | = | 86.3428 |  | ms, | k | = | 3
Ealreq = |  |  | 48587.1707 |  | x | 1 |  | x | 3 | x | ( | 3 | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
Hence, highest Ealreq for Differential & Distance functions at | [7 empty] | Rct: -; Rl: A Tap =; Sr: #VALUE! |  | V
Therefore, the required knee point voltage of the CT.
(Vk in terms of Ealreq as per the Manufacturer )
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: #VALUE! |  | x | 0.8
[8 empty] | +: =; Sr: #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | Required Vk
|  |  |  | 200 |  | #VALUE! | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
| T1 |  | Core1 |  | 0 |  | (Diff. + Dist.) | [10 empty] | Connected devices: | RED670
| 0 | [17 empty] | 0
[7 empty] | Tap-1 | k: Tap-2; (: Tap-3 |  |  | 0
| CT Ratio: | [5 empty] | 2500 | k: -; (: -; +: /; Rl: 1; +: A
| Class of Accuracy: | [6 empty] | (: PX-A
| CT Resistance: | [6 empty] | x: Rct<; (: -; +: W
| Knee Point Voltage: | [6 empty] | x: Vk>; (: -; +: V |  |  |  |  | Highest Vk required = |  | #VALUE!
| Magnetizing Current: | [6 empty] | x: I0<; (: -; +: mA at Vk
Other Burdens on same CT core:
| Burden of |  | RED670 |  |  |  | Sr' | x: =; k: 0.02; (: VA; +: Lead + Other resisitance connected
| Burden of |  | 0 |  |  |  |  | x: =; k: 0; (: VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | Rl | = | Sl | / ( | Isn | x | Isn | )
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Total lead + other burden | [5 empty] | Sl | = | 1.077 |  | VA |  | =: =; Sl: 1.077; Isn: W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer. Ref Annexure-B
For Close-in faults:
Ealreq = |  |  |  |  | Ikmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
Ipn | bar: / ( to x
For Through faults:
Ealreq = |  |  | 2 | x | Itmax |  | x | Isn |  | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
Ipn | bar: / ( to x
| Equivalent Secondary emf. Required | [11 empty] | Sl: Ealreq
| CT primary rated current(A) | [11 empty] | Sl: Ipn; / (: =; Isn: -; Isn: A
| Max. primary fundamental frequency fault current for close-in faults | [11 empty] | Sl: Ikmax; / (: =; Isn: 50000; Isn: A
| Max. primary fundamental frequency fault current for through fault | [13 empty] | Itmax | = | 47858.0776 |  | A | 3-phase
[16 empty] | = | 48245.339 |  | A | 1-phase
| CT secondary rated current | [11 empty] | Sl: Isn; / (: =; Isn: 1; Isn: A
| Relay rated current | [11 empty] | Sl: Ir; / (: =; Isn: 1; Isn: A
| CT secondary winding resistance. | [11 empty] | Sl: Rct; / (: =; Isn: -; Isn: W
| Lead Resistance of the current loop from the CT to Relay | [11 empty] | Sl: Rl; / (: =; Isn: 1.097; Isn: W
| Burden of RED 670 Relay | [11 empty] | Sl: Sr; / (: =; Isn: 0.02; Isn: VA
For Close-in faults:
Ealreq = |  |  |  |  | 50000 |  | x | 1 |  | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
- | bar: / ( to x
|  | = | #VALUE! |  | V
For Through faults (3-ph):
Ealreq = |  |  | 2 | x | 47858.0776 |  | x | 1 |  | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
For Through faults (1-ph):
Ealreq = |  |  | 2 | x | 48245.339 |  | x | 1 |  | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
- | bar: / ( to x
|  | = | #VALUE! |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
The CT secondary limiting e.m.f (Eal) should meet the following requirements as per Relay manufacturer. Ref Annexure-B
For Close-in faults:
Ealreq = |  |  | Ikmax |  | x | Isn |  | x | a | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(1)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
For Endzone-1 faults:
Ealreq = |  |  | Ikzone-1 |  | x | Isn |  | x | k | x | ( | Rct | + | Rl | + | Sr |  |  | ) | ---(2)
[6 empty] | Ipn | [10 empty] | x | Ir | bar: Sr
| Equivalent Secondary emf. Required | [6 empty] | +: Ealreq
| CT primary rated current(A) | [6 empty] | +: Ipn; Sr: = | - |  | A
| Max. primary fundamental frequency fault current for close-in faults | [6 empty] | +: Ikmax; Sr: = | 50000 |  | A
| Max. primary fundamental frequency fault current for zone-1 faults | [6 empty] | +: Ikzone-1; Sr: = | 48271.7306 |  | A | 3-phase
[17 empty] | 48587.1707 |  | A | 1-phase | bar: Sr
| CT secondary rated current . | [6 empty] | +: Isn; Sr: = | 1 |  | A
| Relay rated current | [15 empty] | 1 |  | A | bar: + to Sr
| CT secondary winding resistance. | [6 empty] | +: Rct; Sr: = | - |  | W
| Lead resistance between relay and CT sec. Terminals (2 way ) | [15 empty] | 1.097 |  | W | bar: + to Sr
| Burden of RED 670 Relay | [15 empty] | 0.02 |  | VA | bar: + to Sr
High Speed Distance : Quadrilateral Characteristic
Factor for the Function of the primary time constant for the DC component in the fault current
[7 empty] | For the primary time constant tp | x: <= 400ms; x: :; (: a; +: =; Sr: 1
Factor for Function of the primary time constant for the DC component in the fault current
for a three phase fault at the set reach component in the fault current for of zone-1
[7 empty] | For the primary time constant tp | x: <= 200ms; x: :; (: k; +: =; Sr: 3
For Close-in faults:
[6 empty] | Since System tp |  |  |  | = | 127.2727 |  | ms, | a | = | 1
Ealreq = |  |  | 50000 |  | x | 1 |  | x | 1 | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(1)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
For Endzone-1 3-ph faults:
|  |  |  | Since 3-ph tp for this fault | [5 empty] | = | 111.098 |  | ms, | k | = | 3
Ealreq = |  |  | 48271.7306 |  | x | 1 |  | x | 3 | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
For Endzone-1 1-ph faults:
|  |  |  | Since 1-ph tp for this fault | [5 empty] | = | 86.3428 |  | ms, | k | = | 0
Ealreq = |  |  | 48587.1707 |  | x | 1 |  | x | 0 | x | ( | - | + | 1.097 | + | 0.02 |  |  | ) | ---(2)
[6 empty] | - | [10 empty] | x | 1 | bar: Sr
|  | = | #VALUE! |  | V
Hence, highest Ealreq for Differential & Distance functions at | [7 empty] | Rct: -; Rl: A Tap =; Sr: #VALUE! |  | V
Therefore, the required knee point voltage of the CT.
(Summary of CT requirements for ABB relays, February 2008, formula no. 29, page 17/18)
[8 empty] | Rl: Vk; +: =; Sr: Ealreq |  | x | 0.8
[8 empty] | +: =; Sr: #VALUE! |  | x | 0.8
[8 empty] | +: =; Sr: #VALUE! |  | V
|  |  | Available Vk |  |  | #VALUE! | Required Vk
|  |  |  | - |  | #VALUE! | #VALUE!
[5 empty] | Hence CT is: |  | #VALUE!
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | x: Class; x: CT Resistance (W) @ 75OC; Rct: Limiting Secondary Voltage (Ual), V; Rl: Mag. Current (Io), mA at Vk; Sr: Relay / Instrument Type |  | CT Suitability
T1 | Core1 |  | 2500 |  | 1 | 120 | 6 | x: PX-A; x: 5; Rct: 3750; Rl: 60; Sr: RED670 |  | Suitably Dimensioned
|  |  | - | [14 empty] | - | bar: x; Rct; Rl
|  |  | - | [14 empty] | - | bar: x; Rct; Rl

## IFP2 P545 (4) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | Line Protection(HVDC FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core2 | [14 empty] | Connected devices: | P545
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-A
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 3750 |  | V | [12 empty] | Highest Vk required = | 2896.048
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P545 |  |  |  | Sr' | = | 0.02 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | Sl | = | 1.077 |  | VA
| Resisitance of the relay: | [10 empty] | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.02 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.02; Resisitance of the relay: Ir: W |  |  |  |  | = | 1.077 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, 2Rl |  |  | = | 0.02 |  | + | 1.077 |  | = | 1.097 |  | W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The knee point voltage of the CTs should comply with the minimum requirements of the formulae shown below:
| Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | ) | [9 empty] | …1
A constant depending on the maximum value of through fault current, If (as a multiple of In) and the primary system X/R ratio. K is determined as follows:
1 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 150% (k2 typically set at 150% for two-ended current differential schemes):
| When | ( | if |  | x | X/R | ) | ≤ | ( | 1000 | x | In | ) | [6 empty] | ...cond.1
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.07 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 1000 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 2600 | x | In | ) | …cond.2
| K | = | 107
2 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 100% (k2 typically set at 100% for tapped lines)
| When | ( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [6 empty] | ...cond.3
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) | …cond.4
| K | = | 256
| Resisitance of the relay: Rr: Maximum through fault current | [7 empty] | If |  | = | 50000 |  | A
| Resisitance of the relay: Rr: CT Primary Current | [7 empty] | Ipn |  | = | 2500 |  | A
| Resisitance of the relay: Rr: Maximum through fault current (referred to secondary) | [7 empty] | if |  | = | 20 |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [7 empty] | Rct |  | = | 5 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [7 empty] | 2Rl |  | = | 1.097 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [7 empty] | In |  | = | 1 |  | A
| Resisitance of the relay: Rr: Primary X/R ratio | [7 empty] | X/R |  | = | 40
| Resisitance of the relay: Rr: Enter the setting K2: | [10 empty] | 150 |  | %
| Checking condition |  |  |  | 1 & 2
( | if |  | x | X/R | ) | ≤ | ( | 1000 | x | In | ) | [8 empty] | ...cond.1
( | 20 |  | x | 40 | ) | ≤ | ( | 1000 | x | 1 | )
| Resisitance of the relay: Sr': 800; Resisitance of the relay: x: ≤; Resisitance of the relay: ): 1000 | [9 empty] | … | TRUE
| If | …cond.1 |  | is TRUE, the value of K must be highest of:
|  | K | ≥ | 40 | + | 0.07 | x ( | if |  | x | X/R | ) |  | Hence K |  | = | 96
|  |  | ≥ | 40 | + | 0.07 | x ( | 20 |  | x | 40 | )
|  |  | ≥ | 96
| OR | K | = | 65
( | 1000 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 2600 | x | In | ) |  |  | ...cond.2
( | 1000 | x | 1 | ) | < | ( | 20 |  | x | 40 | ) | ≤ | ( | 2600 | x | 1 | )
| Resisitance of the relay: =: 1000; Resisitance of the relay: Ir: <; Resisitance of the relay: ): 800 |  |  |  | ≤ |  | 2600 |  |  |  | … | FALSE
| Resisitance of the relay: Rr: If; Resisitance of the relay: =: …cond.2; Resisitance of the relay: / (: is TRUE, the value of K | = | 107 |  |  | Hence, final value of K |  |  |  |  | = | 96
Hence, Vk required for Diff. function:
|  |  | Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | )
|  |  |  | ≥ | 96 | x | 1 | x ( | 5 | + | 1.097 | )
|  |  |  | ≥ | 585.3142 |  | V
|  | Available Vk |  |  | > | Required Vk
|  |  | 3750 |  | > | 585.3142
|  |  |  | Hence CT is: |  | Suitably Dimensioned
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
For Close-in faults:
The calculation must be performed for all cables and lines where the source impedance ratio (SIR) may be less than SIR = 2.
| Resisitance of the relay: Ir: SIR; Resisitance of the relay: x: =; Resisitance of the relay: Ir: 27.7826 |  | Since SIR is >2, the below calculation is not applicable
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: x: Kmax; Resisitance of the relay: ): = | Fixed Dimentioning Factory = always 1.4 | [8 empty] | = | 1.4
| Resisitance of the relay: x: Ifmax; Resisitance of the relay: ): = | Max secondary phase-fault current | [8 empty] | = | 20 |  | A
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 1.4 | x | 20 |  | x | ( | 5 | + | 1.097 | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 170.7166 | Volts
Zone-1 reach point accuracy (RPA):
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: Sr': KRPA; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Fixed Dimentioning Factory = always 0.6 | [9 empty] | = | 0.6
| Resisitance of the relay: Sr': IFZ1; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Max secondary phase-fault current at Zone 1 reach point | [9 empty] | = | 19.3087 |  | A
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
|  | Vk | ≥ | 0.6 |  | x | 19.3087 |  | x ( | 1 | + | 40 | ) x ( | 5 | + | 1.097 | )
|  | Vk | ≥ | 2896.048 |  | Volts
| Resisitance of the relay: Rr: Hence, highest Vk required for Diff. & Dist. Functions: |  |  |  | 2896.048 |  | Volts
|  | Available Vk |  |  | > | Required Vk
|  |  | 3750 |  | > | 2896.048
|  |  |  | Hence CT is: |  | Suitably Dimensioned
| Resisitance of the relay: Rr: T1; Resisitance of the relay: Sr': Core2; Resisitance of the relay: Ir: 0; Resisitance of the relay: Ir: 0 | [9 empty] | Connected devices: | P545
| Resisitance of the relay: Rr: 0; Resisitance of the relay: Sr': 0 | [10 empty] | 0
| Resisitance of the relay: Ir: Tap-1 | Tap-2 |  | Tap-3 | [7 empty] | 0
| Resisitance of the relay: Rr: CT Ratio:; Resisitance of the relay: Ir: 2500 | - |  | - |  | / | 1 | A
| Resisitance of the relay: Rr: Class of Accuracy: | PX-A
| Resisitance of the relay: Rr: CT Resistance:; Resisitance of the relay: ): Rct< | 10 |  | W
| Resisitance of the relay: Rr: Knee Point Voltage:; Resisitance of the relay: ): Vk> | 3000 |  | V | [10 empty] | Highest Vk required = | #VALUE!
| Resisitance of the relay: Rr: Magnetizing Current:; Resisitance of the relay: ): I0< | 30 |  | mA at Vk
Other Burdens on same CT core:
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': P545; Resisitance of the relay: Ir: Sr'; Resisitance of the relay: ): = | 0.02 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Total lead burden; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Total lead + other burden; Resisitance of the relay: Ir: Sl; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Resisitance of the relay: |  |  |  | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.02 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.02; Resisitance of the relay: Ir: W |  |  |  |  | = | 1.077 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, 2Rl |  |  | = | 0.02 |  | + | 1.077 |  | = | 1.097 |  | W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The knee point voltage of the CTs should comply with the minimum requirements of the formulae shown below:
| Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | ) | [9 empty] | …1
A constant depending on the maximum value of through fault current, If (as a multiple of In) and the primary system X/R ratio. K is determined as follows:
1 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 150% (k2 typically set at 150% for two-ended current differential schemes):
| When | ( | if |  | x | X/R | ) | ≤ | ( | 1000 | x | In | ) | [6 empty] | ...cond.1
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.07 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 1000 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 2600 | x | In | ) | …cond.2
| K | = | 107
2 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 100% (k2 typically set at 100% for tapped lines)
| When | ( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [6 empty] | ...cond.3
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) | …cond.4
| K | = | 256
| Resisitance of the relay: Rr: Maximum through fault current | [7 empty] | If |  | = | 50000 |  | A
| Resisitance of the relay: Rr: CT Primary Current | [7 empty] | Ipn |  | = | - |  | A
| Resisitance of the relay: Rr: Maximum through fault current (referred to secondary) | [7 empty] | if |  | = | #VALUE! |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [7 empty] | Rct |  | = | 10 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [7 empty] | 2Rl |  | = | 1.097 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [7 empty] | In |  | = | 1 |  | A
| Resisitance of the relay: Rr: Primary X/R ratio | [7 empty] | X/R |  | = | 40
| Resisitance of the relay: Rr: Enter the setting K2: | [10 empty] | 150 |  | %
| Checking condition |  |  |  | 1 & 2
( | if |  | x | X/R | ) | ≤ | ( | 1000 | x | In | ) | [8 empty] | ...cond.1
( | #VALUE! |  | x | 40 | ) | ≤ | ( | 1000 | x | 1 | )
| Resisitance of the relay: Sr': #VALUE!; Resisitance of the relay: x: ≤; Resisitance of the relay: ): 1000 | [9 empty] | … | #VALUE!
| If | …cond.1 |  | is TRUE, the value of K must be highest of:
|  | K | ≥ | 40 | + | 0.07 | x ( | if |  | x | X/R | ) |  | Hence K |  | = | #VALUE!
|  |  | ≥ | 40 | + | 0.07 | x ( | #VALUE! |  | x | 40 | )
|  |  | ≥ | #VALUE!
| OR | K | = | 65
( | 1000 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 2600 | x | In | ) |  |  | ...cond.2
( | 1000 | x | 1 | ) | < | ( | #VALUE! |  | x | 40 | ) | ≤ | ( | 2600 | x | 1 | )
| Resisitance of the relay: =: 1000; Resisitance of the relay: Ir: <; Resisitance of the relay: ): #VALUE! |  |  |  | ≤ |  | 2600 |  |  |  | … | #VALUE!
| Resisitance of the relay: Rr: If; Resisitance of the relay: =: …cond.2; Resisitance of the relay: / (: is TRUE, the value of K | = | 107 |  |  | Hence, final value of K |  |  |  |  | = | #VALUE!
Hence, Vk required for Diff. function:
|  |  | Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | )
|  |  |  | ≥ | #VALUE! | x | 1 | x ( | 10 | + | 1.097 | )
|  |  |  | ≥ | #VALUE! |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
For Close-in faults:
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: x: Kmax; Resisitance of the relay: ): = | Fixed Dimentioning Factory = always 1.4 | [8 empty] | = | 1.4
| Resisitance of the relay: x: Ifmax; Resisitance of the relay: ): = | Max secondary phase-fault current | [8 empty] | = | #VALUE! |  | A
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 1.4 | x | #VALUE! |  | x | ( | 10 | + | 1.097 | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: #VALUE! | Volts
Zone-1 reach point accuracy (RPA):
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: Sr': KRPA; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Fixed Dimentioning Factory = always 0.6 | [9 empty] | = | 0.6
| Resisitance of the relay: Sr': IFZ1; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Max secondary phase-fault current at Zone 1 reach point | [9 empty] | = | #VALUE! |  | A
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
|  | Vk | ≥ | 0.6 |  | x | #VALUE! |  | x ( | 1 | + | 40 | ) x ( | 10 | + | 1.097 | )
|  | Vk | ≥ | #VALUE! |  | Volts
| Resisitance of the relay: Rr: Hence, highest Vk required for Diff. & Dist. Functions: |  |  |  | #VALUE! |  | Volts
|  | Available Vk |  |  | #VALUE! | Required Vk
|  |  | 3000 |  | #VALUE! | #VALUE!
|  |  |  | Hence CT is: |  | #VALUE!
| Resisitance of the relay: Rr: T1; Resisitance of the relay: Sr': Core2; Resisitance of the relay: Ir: 0; Resisitance of the relay: Ir: 0 | [9 empty] | Connected devices: | P545
| Resisitance of the relay: Rr: 0 | [10 empty] | 0
| Resisitance of the relay: Ir: Tap-1 | Tap-2 |  | Tap-3 | [7 empty] | 0
| Resisitance of the relay: Rr: CT Ratio:; Resisitance of the relay: Ir: 2500 | - |  | - |  | / | 1 | A
| Resisitance of the relay: Rr: Class of Accuracy: |  |  | PX-A
| Resisitance of the relay: Rr: CT Resistance: |  | Rct< | - |  | W
| Resisitance of the relay: Rr: Knee Point Voltage: |  | Vk> | - |  | V | [8 empty] | Highest Vk required = | #VALUE!
| Resisitance of the relay: Rr: Magnetizing Current: |  | I0< | - |  | mA at Vk
Other Burdens on same CT core:
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': P545; Resisitance of the relay: Ir: Sr'; Resisitance of the relay: ): = | 0.02 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Total lead burden; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Total lead + other burden; Resisitance of the relay: Ir: Sl; Resisitance of the relay: ): = | 1.077 |  | VA
| Resisitance of the relay: Rr: Resisitance of the relay: |  |  |  | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.02 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 1.077 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.02; Resisitance of the relay: Ir: W |  |  |  |  | = | 1.077 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, 2Rl |  |  | = | 0.02 | + | 1.077 | = | 1.097 | W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The knee point voltage of the CTs should comply with the minimum requirements of the formulae shown below:
| Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | ) | [9 empty] | …1
A constant depending on the maximum value of through fault current, If (as a multiple of In) and the primary system X/R ratio. K is determined as follows:
1 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 150% (k2 typically set at 150% for two-ended current differential schemes):
| When | ( | if |  | x | X/R | ) | ≤ | ( | 1000 | x | In | ) | [6 empty] | ...cond.1
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.07 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 1000 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 2600 | x | In | ) | …cond.2
| K | = | 107
2 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 100% (k2 typically set at 100% for tapped lines)
| When | ( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [6 empty] | ...cond.3
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) | …cond.4
| K | = | 256
| Resisitance of the relay: Rr: Maximum through fault current | [7 empty] | If |  | = | 50000 |  | A
| Resisitance of the relay: Rr: CT Primary Current | [7 empty] | Ipn |  | = | - |  | A
| Resisitance of the relay: Rr: Maximum through fault current (referred to secondary) | [7 empty] | if |  | = | #VALUE! |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [7 empty] | Rct |  | = | - |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [7 empty] | 2Rl |  | = | 1.097 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [7 empty] | In |  | = | 1 |  | A
| Resisitance of the relay: Rr: Primary X/R ratio | [7 empty] | X/R |  | = | 40
| Resisitance of the relay: Rr: Enter the setting K2: | [10 empty] | 150 |  | %
| Checking condition |  |  |  | 1 & 2
( | if |  | x | X/R | ) | ≤ | ( | 1000 | x | In | ) | [8 empty] | ...cond.1
( | #VALUE! |  | x | 40 | ) | ≤ | ( | 1000 | x | 1 | )
| Resisitance of the relay: Sr': #VALUE!; Resisitance of the relay: x: ≤; Resisitance of the relay: ): 1000 | [9 empty] | … | #VALUE!
| If | …cond.1 |  | is TRUE, the value of K must be highest of:
|  | K | ≥ | 40 | + | 0.07 | x ( | if |  | x | X/R | ) |  | Hence K |  | = | #VALUE!
|  |  | ≥ | 40 | + | 0.07 | x ( | #VALUE! |  | x | 40 | )
|  |  | ≥ | #VALUE!
| OR | K | = | 65
( | 1000 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 2600 | x | In | ) |  |  | ...cond.2
( | 1000 | x | 1 | ) | < | ( | #VALUE! |  | x | 40 | ) | ≤ | ( | 2600 | x | 1 | )
| Resisitance of the relay: =: 1000; Resisitance of the relay: Ir: <; Resisitance of the relay: ): #VALUE! |  |  |  | ≤ |  | 2600 |  |  |  | … | #VALUE!
| Resisitance of the relay: Rr: If; Resisitance of the relay: =: …cond.2; Resisitance of the relay: / (: is TRUE, the value of K | = | 107 |  |  | Hence, final value of K |  |  |  |  | = | #VALUE!
Hence, Vk required for Diff. function:
|  |  | Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | )
|  |  |  | ≥ | #VALUE! | x | 1 | x ( | - | + | 1.097 | )
|  |  |  | ≥ | #VALUE! |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
For Close-in faults:
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: x: Kmax; Resisitance of the relay: ): = | Fixed Dimentioning Factory = always 1.4 | [8 empty] | = | 1.4
| Resisitance of the relay: x: Ifmax; Resisitance of the relay: ): = | Max secondary phase-fault current | [8 empty] | = | #VALUE! |  | A
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 1.4 | x | #VALUE! |  | x | ( | - | + | 1.097 | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: #VALUE! | Volts
Zone-1 reach point accuracy (RPA):
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: Sr': KRPA; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Fixed Dimentioning Factory = always 0.6 | [9 empty] | = | 0.6
| Resisitance of the relay: Sr': IFZ1; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Max secondary phase-fault current at Zone 1 reach point | [9 empty] | = | #VALUE! |  | A
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
|  | Vk | ≥ | 0.6 |  | x | #VALUE! |  | x ( | 1 | + | 40 | ) x ( | - | + | 1.097 | )
|  | Vk | ≥ | #VALUE! |  | Volts
| Resisitance of the relay: Rr: Hence, highest Vk required for Diff. & Dist. Functions: |  |  |  | #VALUE! |  | Volts
|  | Available Vk |  |  | #VALUE! | Required Vk
|  |  | - |  | #VALUE! | #VALUE!
|  |  |  | Hence CT is: |  | #VALUE!
Summary of available CT parameters and its suitability
CT / Core | Resisitance of the relay: Sr': Ratio (A); Resisitance of the relay: x: CT Cable m/mm2; Resisitance of the relay: ): Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) |  | Connected Devices |  | CT Suitability
T1 | Core2 |  | 2500 |  | 1 | 75 | 6 | PX-A |  | 5 |  | 3750 |  | 60 |  | P545 |  | Suitably Dimensioned
[10 empty] | - |  | - |  | - | bar: Resisitance of the relay: Sr'
[10 empty] | - |  | - |  | - | bar: Resisitance of the relay: Sr'

## BUP BCU(4) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AK | Checked By |  |  | LN | Line Protection(HVDC FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core3 | [14 empty] | Connected devices: | REF650
REC670
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | IDM+9
| CT Ratio: | [5 empty] | 2500 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | 5P20
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> |  |  | V | [12 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA |  | CT internal Burden
| Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA
| Burden of |  | IDM+9 |  |  |  |  | = | 0.058 |  | VA |  | PE | = | In | x | In | x | Rct
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead + other burden | [5 empty] | PL | = | 1.175 |  | VA |  |  | = | 5 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula: | [21 empty] | The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2500 |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 0 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 5 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN | = | 30
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | 0 |  | x | 1 | ) / | 20 | ) - | 5
|  |  | = | -5 |  | VA
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 50000 |  | / | 2500
[5 empty] | = | 20
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 5 | + | 30 | ) / ( | 5 | + | 1.175 | )
[5 empty] | = | 113.3599
|  |  |  | Available Kssc' | = =: >; 20 n: Required Kssc'
|  |  | 113.3599 |  | = =: >; 20 n: 20
|  |  |  | Hence CT is: | 20 n: Suitably Dimentioned
| T1 |  | Core3 |  | 20 x ( (: 0 |  |  | Connected devices: | REF650
| 0 | [17 empty] | REC670
[5 empty] | 20 x ( (: Tap-1; 20 +: Tap-2; 20 ) / (: Tap-3 |  |  |  | IDM+9
| CT Ratio: |  |  |  | 20 x ( (: 2500; 20 +: -; 20 ) / (: -; 20 +: /; 20 PL: 1; 20 ): A
| Class of Accuracy: |  |  |  | 20 +: 5P20
| CT Resistance: |  |  |  | 20 PE: Rct<; 20 +: -; 20 ) / (: W
| Knee Point Voltage: |  |  |  | 20 PE: Vk>; 20 +: -; 20 ) / (: V | [6 empty] | #VALUE!
| Magnetizing Current: |  |  |  | 20 PE: I0<; 20 +: -; 20 ) / (: mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  | 20 PE: =; 20 +: 0.02; 20 ) / (: VA; 20 +: CT internal Burden
| Burden of |  | REC670 |  | 20 PE: =; 20 +: 0.02; 20 ) / (: VA
| Burden of |  | IDM+9 |  | 20 PE: =; 20 +: 0.058; 20 ) / (: VA; 20 +: PE; 20 PL: =; 20 ): In | x | In | x | Rct
| Total lead burden |  |  |  | 20 PE: =; 20 +: 1.077; 20 ) / (: VA; 20 PL: =; 20 ): 1 | x | 1 | x | -
| Total lead + other burden |  |  |  | 20 x ( (: PL; 20 PE: =; 20 +: 1.175; 20 ) / (: VA; 20 PL: =; 20 ): #VALUE! |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | - |  | V
|  | Internal Burden, | [13 empty] | PE | = | #VALUE! |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | - |  | x | 1 | ) / | 20 | ) - | #VALUE!
|  |  | = | #VALUE! | bar: 20 n
ABB
|  |  |  | Required Kssc' | = =: =; 20 n: Itkmax; 20 PE: /; 20 +: Ipn
[5 empty] | = | 50000 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | #VALUE! | + | #VALUE! | ) / ( | #VALUE! | + | 1.175 | )
[5 empty] | = | #VALUE!
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | #VALUE! |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
ABB
| T1 |  | Core3 |  | #VALUE! x ( (: 0 |  |  | Connected devices: | REF650
| 0 | [17 empty] | REC670
[5 empty] | #VALUE! x ( (: Tap-1; #VALUE! +: Tap-2; #VALUE! ) / (: Tap-3 |  |  |  | IDM+9
| CT Ratio: |  |  |  | #VALUE! x ( (: 2500; #VALUE! +: -; #VALUE! ) / (: -; #VALUE! +: /; #VALUE! PL: 1; #VALUE! ): A
| Class of Accuracy: |  |  |  | #VALUE! ) / (: 5P20
| CT Resistance: |  |  |  | #VALUE! PN: Rct<; #VALUE! ) / (: -; #VALUE! +: W
| Knee Point Voltage: |  |  |  | #VALUE! PN: Vk>; #VALUE! ) / (: -; #VALUE! +: V | [6 empty] | #VALUE!
| Magnetizing Current: |  |  |  | #VALUE! PN: I0<; #VALUE! ) / (: -; #VALUE! +: mA at Vk
Other Burdens on same CT core:
| Burden of |  | REF650 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA; #VALUE! +: CT internal Burden
| Burden of |  | REC670 |  | #VALUE! PE: =; #VALUE! +: 0.02; #VALUE! ) / (: VA
| Burden of |  | IDM+9 |  | #VALUE! PE: =; #VALUE! +: 0.058; #VALUE! ) / (: VA; #VALUE! +: PE; #VALUE! PL: =; #VALUE! ): In | x | In | x | Rct
| Total lead burden |  |  |  | #VALUE! PE: =; #VALUE! +: 1.077; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): 1 | x | 1 | x | -
| Total lead + other burden |  |  |  | #VALUE! x ( (: PL; #VALUE! PE: =; #VALUE! +: 1.175; #VALUE! ) / (: VA; #VALUE! PL: =; #VALUE! ): #VALUE! |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | - |  | V
|  | Internal Burden, | [13 empty] | PE | = | #VALUE! |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.175 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | Rated CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | - |  | x | 1 | ) / | 20 | ) - | #VALUE!
|  |  | = | #VALUE! | bar: #VALUE! n
ABB
|  |  |  | Required Kssc' | = =: =; #VALUE! n: Itkmax; #VALUE! PE: /; #VALUE! +: Ipn
[5 empty] | = | 50000 |  | / | -
[5 empty] | = | #VALUE!
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | #VALUE! | + | #VALUE! | ) / ( | #VALUE! | + | 1.175 | )
[5 empty] | = | #VALUE!
|  |  |  | Available Kssc' | = =: #VALUE!; #VALUE! n: Required Kssc'
|  |  | #VALUE! |  | = =: #VALUE!; #VALUE! n: #VALUE!
|  |  |  | Hence CT is: | #VALUE! n: #VALUE!
ABB
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  | #VALUE! n: CT Cable m/mm2; #VALUE! PE: Class; #VALUE! PN: Rct @ 75OC (Ω); #VALUE! PE: Rated Vk (V); #VALUE! PL: Im @ Vk (mA) | Connected Devices |  | CT Suitability
T1 | Core3 |  | 2500 |  | 1 | 120 | 6 | 5P20 |  | 5 |  | - |  | - |  | REF650 REC670 IDM+9 |  | Suitably Dimentioned
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL
|  |  | - | [14 empty] | - | bar: #VALUE! PN; #VALUE! PE; #VALUE! PL

## BBP FU1 - REB500 (4) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | Line Protection(HVDC FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core4 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | REB500
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 |  |  |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [12 empty] | #REF!
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 5 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.087 |  | VA
CT-Requirements for BB Protection
|  | Maximum Primary Fault Current | [13 empty] | Isc | = | 50000 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2500 |  | A
|  | Rated Voltage | [13 empty] | UN2 | = | 33 |  | kV
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 750 |  | V
|  | Internal Resistance CT | [13 empty] | Rct | = | 5 |  | VA
|  | Conn. Lead + Relay Burden | [13 empty] | RL | = | 1.087 |  | VA
|  | Rated Secondary Current, | [13 empty] | Isc | = | 1 |  | A
|  | Nominal Frequency of the network | [13 empty] | fn | = | 50
Required OC factor condition. 1:
At Max. Through fault current CT’s shall not saturate for currents below 5 times rated current.
[8 empty] | n' | = | Isc
5 * Ipn
Required OC factor Condition 2:
n2' >= 10 for TN <=120 msec
n2' >= 20 for 120ms <= TN <=300 ms
| Where, |  | n' = Required OC factor
Isc = max. bus fault current
Ipn = Rated primary current (A)
[23 empty] | ** | Rated Bus fault current
Required OC factor condition 1:
|  | n'(1) | = | 50000
5 x 2500
|  | n'(1) | = | 4
Required OC factor condition 2:
|  |  |  | TN = | 1 |  | X | X
[6 empty] | 2* ϖ* fn |  | R
[5 empty] | 1 |  |  |  | x | 15
|  |  | TN | = | 2 * 3.14 * 50
|  |  |  | = | 0.047771 |  | sec
|  |  | TN | = | 47.7707 |  | ms
| Hence n'(2) 10 |  |  | = | 10
Required OC factor n' >= max( n'(1) ; n'(2))
n' >=max(4 ; 10)
Therefore
|  | n' | = | 10 |  | Necessary Condition
Required secondary equivalent limiting secondary e.m.f
Eal >= n' *(RCT+RL+Rr)*Isn
| = | 10 | x | ( | 5 |  | + | 1.087 | + | 0.01 | ) | x | 1
| Eal | = | 60.9702 | V
| According to IEC 61869 class PX | [7 empty] | Eknee |  | > |  | 0.8*Eal
[11 empty] | = |  | 48.7762
[5 empty] | With design margin 120% | [5 empty] | = |  | 58.5314
[10 empty] | Available Vk | > | Required Vk
[8 empty] | 750 |  |  | > | 58.5314
[10 empty] | Hence CT is: |  | Suitable Dimensions
| T1 |  | Core4 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | REB500
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | 0 |  | - |  | / | 1 | A
| Class of Accuracy: | [7 empty] | PX-B
| CT Resistance: | [6 empty] | Rct< | 9.3 |  | W
| Knee Point Voltage: | [6 empty] | Vk> | 500 |  | V | [10 empty] | Required Vk
| Magnetizing Current: | [6 empty] | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 9.3
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | 9.3 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.087 |  | VA
CT-Requirements for BB Protection
|  | Maximum Primary Fault Current | [13 empty] | Isc | = | 31500 |  | A | **
|  | CT Primary Current, | [13 empty] | Ipn | = | 0 |  | A
|  | Rated Voltage | [13 empty] | UN2 | = | 33 |  | kV
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 500 |  | V
|  | Internal Resistance CT | [13 empty] | Rct | = | 9.3 |  | VA
|  | Conn. Lead + Relay Burden | [13 empty] | RL | = | 1.087 |  | VA
|  | Rated Secondary Current, | [13 empty] | Isc | = | 1 |  | A
|  | Nominal Frequency of the network | [13 empty] | fn | = | 50
Required OC factor condition. 1:
At Max. Through fault current CT’s shall not saturate for currents below 5 times rated current.
[8 empty] | n' | = | Isc
5 * Ipn
Required OC factor Condition 2:
n2' >= 10 for TN <=120 msec
n2' >= 20 for 120ms <= TN <=300 ms
Where,
n' = Required OC factor
Isc = max. bus fault current
Ipn = Rated primary current (A)
[10 empty] | ** | Rated Bus fault current
Required OC factor condition 1:
|  | n'(1) | = | 31500
5 x 0
|  | n'(1) | = | #DIV/0!
Required OC factor condition 2:
|  |  |  | TN = | 1 |  | X | X
[6 empty] | 2* ϖ* fn |  | R
| As per Transco Standard for 33kV system X/R | [11 empty] | = | #REF!
[5 empty] | 1 |  |  |  | x | #REF!
|  |  | TN | = | 2 * 3.14 * 50
|  |  |  | = | #REF! |  | sec
|  |  | TN | = | #REF! |  | ms
| Hence n'(2) 10 |  |  | = | 10
Required OC factor n' >= max( n'(1) ; n'(2))
n' >=max(3.15 ; 10)
Therefore
|  | n' | = | #DIV/0! |  | Necessary Condition
Required secondary equivalent limiting secondary e.m.f
Eal >= n' *(RCT+RL+Rr)*Isn
| = | #DIV/0! | x | ( | 9.3 |  | + | 1.087 | + | 0.01 | ) | x | 1
| Eal | = | #DIV/0! | V
| According to IEC 61869 class PX | [7 empty] | Eknee |  | > |  | 0.8*Eal
[11 empty] | = |  | #DIV/0!
[5 empty] | With design margin 120% | [5 empty] | = |  | #DIV/0!
[10 empty] | Available Vk | #DIV/0! | Required Vk
[9 empty] | 500 |  | #DIV/0! | #DIV/0!
[10 empty] | Hence CT is: |  | #DIV/0!
| T1 |  | Core4 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | REB500
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | 0 |  | - |  | / | 1 | A
| Class of Accuracy: | [9 empty] | PX-B
| CT Resistance: | [8 empty] | Rct< | - |  | W
| Knee Point Voltage: | [8 empty] | Vk> | - |  | V | [8 empty] | #VALUE!
| Magnetizing Current: | [8 empty] | I0< | - |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [6 empty] | = | 1.077 |  | VA |  |  | = | #VALUE! |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.087 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 1 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | - |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | - |  | V
|  | Internal Burden, | [13 empty] | PE | = | #VALUE! |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 1.087 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  |  | = | ( ( | 1.3 | x | - |  | x | 1 | ) / | 20 | ) - | #VALUE!
|  |  | = | #VALUE! |  | VA
The CT requirement is as follows:
where
| n' | ³ | n1 |  | --- (i) |  |  |  |  | n' | = | The effective accuracy limiting factor
| n' | ³ | n2 |  | --- (ii) | [5 empty] | = | n x (PN + PE) / (PL + PE)
[10 empty] | n1 | = | Itkmax / (5 x Ipn)
[10 empty] | n2 | = | 10 |  | ...for | TP | £ | 120 | msec
[11 empty] | = | 20 |  | ...for | TP | £ | 300 | msec
Calculation for n1: | [9 empty] | n1 | = | Itmax |  | / ( | 5 | x | Ipn |  | )
[11 empty] | = | 1 |  | / ( | 5 | x | - |  | )
[11 empty] | = | #VALUE!
Calculation for n2: |  |  |  | Since Tp |  | = | #REF! |  | , | n2 | = | #REF!
Calculation for n': | [5 empty] | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[6 empty] | = | 20 | x ( ( | #VALUE! | + | #VALUE! | ) / ( | #VALUE! | + | 1.087 | )
[6 empty] | = | #VALUE!
Checking the conditions ---(i) and ---(ii) mentioned aove:
|  |  | #VALUE! |  | #VALUE! | =: #VALUE!; PE: --- (i)
|  |  | #VALUE! |  | #VALUE! | =: #REF!; PE: --- (ii)
|  |  |  | Hence CT is: |  | =: #VALUE!
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | =: CT Cable m/mm2; x ( (: Class; +: CT Resistance (W) @ 75OC; ) / (: Limiting Secondary Voltage (Ual), V; +: Mag. Current (Io), mA at Vk; ): Relay / Instrument Type |  | CT Suitability
T1 | Core4 |  | 2500 |  | 1 | 120 | 6 | PX-B | #REF! | 5 |  | 750 |  | 60 |  | REB500 |  | Suitable Dimensions
|  |  | 0 | [14 empty] | - | bar: +; ) / (; +
|  |  | - | [14 empty] | - | bar: +; ) / (; +

## P74X-X (4) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | Line Protection(HVDC FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core5 | [14 empty] | Connected devices: | P743
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 2500 | [5 empty] | / | 1 | A
| Class of Accuracy: | [5 empty] | PX-B
| CT Resistance: |  |  |  |  | Rct< | 5 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 750 |  | V | [12 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< | 60 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.177 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 50000 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 2500 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | 20 |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 1.177 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 50000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | 20 |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | 20 |  | x ( | 5 |  | + | 1.177 |  | )
|  |  | = | 61.7702
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 20 |  | x ( | 5 |  | + | 1.177 |  | )
|  |  | = | 123.5404
Adequacy Check
Criteria I
[5 empty] | Available Vk | > | Required Vk |  |  |  | (Criteria I)
|  |  |  | 750 |  | > | 61.7702
[5 empty] | Hence: |  | Criteria I |  | is | Satisfied
Criteria II
[5 empty] | Available Vk | > | Required Vk |  |  |  | (Criteria II)
|  |  |  | 750 |  | > | 123.5404
[5 empty] | Hence: |  | Criteria II |  | is | Satisfied
[5 empty] | Hence CT is: |  | Suitably Dimentioned
| T1 |  | Core5 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | P743
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | 0 |  | 0 |  | / | 1 | A
| Class of Accuracy: | [7 empty] | PX-B
| CT Resistance: | [6 empty] | Rct< |  |  | W
| Knee Point Voltage: | [6 empty] | Vk> |  |  | V | [10 empty] | Under Dimentioned
| Magnetizing Current: | [6 empty] | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.177 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 50000 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 2500 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | 20 |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 1.177 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 50000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | 20 |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | 20 |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | 11.7702
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 20 |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | 23.5404
Adequacy Check
Criteria I
[5 empty] | Available Vk | < | Required Vk |  |  |  | (Criteria I)
|  |  |  | 0 |  | < | 11.7702
[5 empty] | Hence: |  | Criteria I |  | is | Not Satisfied
Criteria II
[5 empty] | Available Vk | < | Required Vk |  |  |  | (Criteria II)
|  |  |  | 0 |  | < | 23.5404
[5 empty] | Hence: |  | Criteria II |  | is | Not Satisfied
[5 empty] | Hence CT is: |  | Under Dimentioned
ABB
| T1 |  | Core5 |  |  |  | (Low Imp. Busbar) | [10 empty] | Connected devices: | P743
0
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3 | [7 empty] | 0
| CT Ratio: | [5 empty] | 2500 |  | 0 |  | 0 |  | / | 1 | A
| Class of Accuracy: | [9 empty] | PX-B
| CT Resistance: | [8 empty] | Rct< |  |  | W
| Knee Point Voltage: | [8 empty] | Vk> |  |  | V | [8 empty] | #DIV/0!
| Magnetizing Current: | [8 empty] | I0< |  |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P743 |  |  |  |  | = | 0.1 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Burden of |  | 0 |  |  |  |  | = | 0 |  | VA
| Total lead burden | [6 empty] | = | 1.077 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 1.177 |  | VA
|  | Max primary fault current (same for all feeders) | [13 empty] | IFmax | = | 50000 |  | A
|  | CT Primary Current | [13 empty] | Ipn | = | 0 |  | A
|  | Max secondary fault current (same for all feeders) | [13 empty] | Ifmax | = | #DIV/0! |  | A
|  | Resistive burden of CT Leads (2Rl) and other connected devices | [13 empty] | Rb' | = | 1.177 |  | W
|  | Max primary contribution from a feeder to an internal fault | [13 empty] | IFmax int | = | 50000 |  | A
|  | Max secondary contribution from a feeder to an internal fault | [13 empty] | Ifmax int | = | #DIV/0! |  | A
The CT requirement is as follows:
Criteria I
| Vk |  | >= | 0.5 | x | Ifmax |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | 0.5 | x | #DIV/0! |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | #DIV/0!
Criteria II
| Vk |  | >= | Ifmax int |  | x ( | Rct |  | + | Rb' |  | )
|  |  | = | #DIV/0! |  | x ( | 0 |  | + | 1.177 |  | )
|  |  | = | #DIV/0!
ABB
Adequacy Check
Criteria I
[5 empty] | Available Vk | #DIV/0! | Required Vk |  |  |  | (Criteria I)
|  |  |  | 0 |  | #DIV/0! | #DIV/0!
[5 empty] | Hence: |  | Criteria I |  | is | #DIV/0!
Criteria II
[5 empty] | Available Vk | #DIV/0! | Required Vk |  |  |  | (Criteria II)
|  |  |  | 0 |  | #DIV/0! | #DIV/0!
[5 empty] | Hence: |  | Criteria II |  | is | #DIV/0!
[5 empty] | Hence CT is: |  | #DIV/0!
ABB
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  |  | CT Cable m/mm2 |  | Class |  | CT Resistance (W) @ 75OC |  | Limiting Secondary Voltage (Ual), V |  | Mag. Current (Io), mA at Vk |  | Relay / Instrument Type |  | CT Suitability
T1 | Core5 |  | 2500 |  | 1 | 120 | 6 | PX-B |  | 5 |  | 750 |  | 60 |  | P743 |  | Suitably Dimentioned
|  |  | - | [6 empty] | - |  | - |  | - |  |  |  | -
|  |  | - | [6 empty] | - |  | - |  | - |  |  |  | -

## CS1 (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | Line Protection(HVDC FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core6 |  |  | (Metering) | [10 empty] | Connected devices: | XC-RACK
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 2000 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.2S
| CT Resistance: |  |  |  | Rct< | 5 |  | W
| Factor of Safety |  |  |  | FS | 10 | [13 empty] | Not suitable
| Rated Burden |  |  |  | PN | 10 |  | VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [9 empty] | rec670 | 100A for 1 S
| Burden of |  | 0 |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 5 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 1.085 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 2000 |  | A
| Internal Burden, | [10 empty] | PE | = | 5 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 1.085 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | Pn | = | 10
| Safety Factor Fs (min) | [11 empty] | = | 20 | [6 empty] | Safety Factor among all connected devices Fs (min)
XC-RACK = 20 A for 0.5 sec Refer annuxure mail received from manufacturer
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 1.085
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 10 | x ( ( | 5 | + | 10 | ) / ( | 5 | + | 1.085 | )
[7 empty] | = | 24.6507
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.085 FS: Total Connected Burden; 1.085 ): …cond.1
[5 empty] | 10 |  | = =: >; 1.085 FS: 1.085; 1.085 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.085 FS: Effective Safety Factor of CT, FS'; 1.085 ): …cond.2
[5 empty] | 20 |  | = =: <; 1.085 FS: 24.6507; 1.085 ): Not satisfied
[6 empty] | Hence CT is: | 1.085 FS: Not suitable
| T1 |  | Core6 |  |  | (Metering) | 1.085 ): Connected devices: | XC-RACK
0
[6 empty] | Tap-1 | 1.085 FS: Tap-2; 1.085 PE: Tap-3
| CT Ratio: |  |  |  |  | 2000 | 1.085 FS: -; 1.085 PE: -; 1.085 PN: /; 1.085 ) / (: 1; 1.085 PE: A
| Class of Accuracy: | [5 empty] | 1.085 FS: 0.2S
| CT Resistance: | [5 empty] | = =: Rct<; 1.085 FS: 5; 1.085 PE: W
| Factor of Safety | [5 empty] | = =: FS; 1.085 FS: 10 |  |  | Suitable Dimensions
| Rated Burden | [5 empty] | = =: PN; 1.085 FS: 5; 1.085 PE: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 1.085 FS: 0.008; 1.085 PE: VA; 1.085 PN: CT internal Burden
| Burden of |  | 0 |  |  |  | = =: =; 1.085 FS: 0; 1.085 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = =: =; 1.085 FS: 1.077; 1.085 PE: VA; 1.085 ) / (: =; 1.085 PE: 5; 1.085 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.085 FS: 1.085; 1.085 PE: VA
| CT Primary Current, | [5 empty] | 1.085 PN: Ipn; 1.085 ) / (: =; 1.085 PE: -; 1.085 PL: A
| Internal Burden, | [5 empty] | 1.085 PN: PE; 1.085 ) / (: =; 1.085 PE: 5; 1.085 PL: VA
| Burden of CT Leads and burden of connected devices | [5 empty] | 1.085 PN: PL; 1.085 ) / (: =; 1.085 PE: 1.085; 1.085 PL: VA
| Rated Secondary Current, | [5 empty] | 1.085 PN: In; 1.085 ) / (: =; 1.085 PE: 1; 1.085 PL: A
| CT Safety Factor | [5 empty] | 1.085 PN: n; 1.085 ) / (: =; 1.085 PE: 10
| Safety Factor among all connected devices Fs (min) | [5 empty] | 1.085 ) / (: =; 1.085 PE: 20; 1.085 PL: **; 1.085 ): Assumed
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.085 +: Fs(min); 1.085 PL: =; 1.085 ): 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.085 FS: Connected devices burden; 1.085 PE: +; 1.085 +: Lead Burden
[7 empty] | = | 1.085
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 10 | x ( ( | 5 | + | 5 | ) / ( | 5 | + | 1.085 | )
[7 empty] | = | 16.4338
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.085 FS: Total Connected Burden; 1.085 ): …cond.1
[5 empty] | 5 |  | = =: >; 1.085 FS: 1.085; 1.085 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.085 FS: Effective Safety Factor of CT, FS'; 1.085 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.085 FS: 16.4338; 1.085 ): Satisfied
[6 empty] | Hence CT is: | 1.085 FS: Suitable Dimensions
| T1 |  | Core6 |  |  | (Metering)
0
[6 empty] | Tap-1 | 1.085 FS: Tap-2; 1.085 PE: Tap-3
| CT Ratio: |  |  |  |  | 2000 | 1.085 FS: -; 1.085 PE: -; 1.085 PN: /; 1.085 ) / (: 1; 1.085 PE: A
| Class of Accuracy: | [5 empty] | 1.085 PE: 0.2S
| CT Resistance: | [5 empty] | 1.085 x ( (: Rct<; 1.085 PE: -; 1.085 PN: W
| Factor of Safety | [18 empty] | #VALUE! | bar: 1.085 x ( ( to 1.085 +
| Rated Burden | [5 empty] | 1.085 x ( (: PN; 1.085 PE: -; 1.085 PN: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 1.085 FS: 0.008; 1.085 PE: VA; 1.085 PN: CT internal Burden
| Burden of |  | 0 |  |  |  | = =: =; 1.085 FS: 0; 1.085 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [5 empty] | = =: =; 1.085 FS: 1.077; 1.085 PE: VA; 1.085 ) / (: =; 1.085 PE: #VALUE!; 1.085 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.085 FS: 1.085; 1.085 PE: VA
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.085 +: Fs(min); 1.085 PL: =; 1.085 ): 20
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.085 FS: CT Int. Burden; 1.085 +: +; 1.085 PN: Connected Burden
[7 empty] | = | #VALUE! |  | + | 1.085
[7 empty] | = | #VALUE!
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | - | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 1.085 | )
[7 empty] | = | #VALUE!
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; #VALUE! FS: Total Connected Burden; #VALUE! ): …cond.1
[5 empty] | - |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; #VALUE! FS: Effective Safety Factor of CT, FS'; #VALUE! ): …cond.2
[5 empty] | 20 |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
[6 empty] | Hence CT is: | #VALUE! FS: #VALUE!
ABB
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; #VALUE! x ( (: CT Resistance (W) @ 75OC; #VALUE! +: Rated Burden VA; #VALUE! +: Relay / Instrument Type; #VALUE! ): CT Suitability
T1 | Core6 |  | 2000 | 1 | 120 | 6 | = =: 0.2S; #VALUE! x ( (: 5; #VALUE! +: 10; #VALUE! ) / (: -; #VALUE! +: XC-RACK; #VALUE! ): Not suitable
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )

## CS2 (hidden)
HITACHI | [5 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[6 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[6 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[13 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  | RB | Line Protection(HVDC FEEDERS) | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core7 |  |  | (Metering) | [10 empty] | Connected devices: | XC-RACK
[6 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: |  |  |  |  | 2000 |  | - |  | - |  | / | 1 | A
| Class of Accuracy: |  |  |  |  | 0.2S
| CT Resistance: |  |  |  | Rct< | 5 |  | W
| Factor of Safety |  |  |  | FS | 10 | [13 empty] | Not suitable
| Rated Burden |  |  |  | PN | 10 |  | VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = | 0.008 |  | VA |  | CT internal Burden | [9 empty] | rec670 | 100A for 1 S
| Burden of |  | 0 |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = | 1.077 |  | VA |  |  | = | 5 |  | VA
| Total lead + other burden |  |  |  |  | PL | = | 1.085 |  | VA
| CT Primary Current, | [10 empty] | Ipn | = | 2000 |  | A
| Internal Burden, | [10 empty] | PE | = | 5 |  | VA
| Burden of CT Leads and burden of connected devices | [10 empty] | PL | = | 1.085 |  | VA
| Rated Secondary Current, | [10 empty] | In | = | 1 |  | A
| CT Safety Factor | [10 empty] | Pn | = | 10
| Safety Factor Fs (min) | [11 empty] | = | 20 | [6 empty] | Safety Factor among all connected devices Fs (min)
XC-RACK = 20 A for 0.5 sec Refer annuxure mail received from manufacturer
|  | Minimum Safety Factor among all connected devices | [12 empty] | Fs(min) | = | 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = | Connected devices burden | [5 empty] | + | Lead Burden
[7 empty] | = | 1.085
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 10 | x ( ( | 5 | + | 10 | ) / ( | 5 | + | 1.085 | )
[7 empty] | = | 24.6507
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.085 FS: Total Connected Burden; 1.085 ): …cond.1
[5 empty] | 10 |  | = =: >; 1.085 FS: 1.085; 1.085 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.085 FS: Effective Safety Factor of CT, FS'; 1.085 ): …cond.2
[5 empty] | 20 |  | = =: <; 1.085 FS: 24.6507; 1.085 ): Not satisfied
[6 empty] | Hence CT is: | 1.085 FS: Not suitable
| T1 |  | Core7 |  |  | (Metering) | 1.085 ): Connected devices: | XC-RACK
0
[6 empty] | Tap-1 | 1.085 FS: Tap-2; 1.085 PE: Tap-3
| CT Ratio: |  |  |  |  | 2000 | 1.085 FS: -; 1.085 PE: -; 1.085 PN: /; 1.085 ) / (: 1; 1.085 PE: A
| Class of Accuracy: | [5 empty] | 1.085 FS: 0.2S
| CT Resistance: | [5 empty] | = =: Rct<; 1.085 FS: 5; 1.085 PE: W
| Factor of Safety | [5 empty] | = =: FS; 1.085 FS: 10 |  |  | Suitable Dimensions
| Rated Burden | [5 empty] | = =: PN; 1.085 FS: 5; 1.085 PE: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 1.085 FS: 0.008; 1.085 PE: VA; 1.085 PN: CT internal Burden
| Burden of |  | 0 |  |  |  | = =: =; 1.085 FS: 0; 1.085 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | 5
| Total lead burden | [5 empty] | = =: =; 1.085 FS: 1.077; 1.085 PE: VA; 1.085 ) / (: =; 1.085 PE: 5; 1.085 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.085 FS: 1.085; 1.085 PE: VA
| CT Primary Current, | [5 empty] | 1.085 PN: Ipn; 1.085 ) / (: =; 1.085 PE: -; 1.085 PL: A
| Internal Burden, | [5 empty] | 1.085 PN: PE; 1.085 ) / (: =; 1.085 PE: 5; 1.085 PL: VA
| Burden of CT Leads and burden of connected devices | [5 empty] | 1.085 PN: PL; 1.085 ) / (: =; 1.085 PE: 1.085; 1.085 PL: VA
| Rated Secondary Current, | [5 empty] | 1.085 PN: In; 1.085 ) / (: =; 1.085 PE: 1; 1.085 PL: A
| CT Safety Factor | [5 empty] | 1.085 PN: n; 1.085 ) / (: =; 1.085 PE: 10
| Safety Factor among all connected devices Fs (min) | [5 empty] | 1.085 ) / (: =; 1.085 PE: 20; 1.085 PL: **; 1.085 ): Assumed
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.085 +: Fs(min); 1.085 PL: =; 1.085 ): 20 |  | **
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.085 FS: Connected devices burden; 1.085 PE: +; 1.085 +: Lead Burden
[7 empty] | = | 1.085
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | 10 | x ( ( | 5 | + | 5 | ) / ( | 5 | + | 1.085 | )
[7 empty] | = | 16.4338
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; 1.085 FS: Total Connected Burden; 1.085 ): …cond.1
[5 empty] | 5 |  | = =: >; 1.085 FS: 1.085; 1.085 ): Satisfied
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; 1.085 FS: Effective Safety Factor of CT, FS'; 1.085 ): …cond.2
[5 empty] | 20 |  | = =: >; 1.085 FS: 16.4338; 1.085 ): Satisfied
[6 empty] | Hence CT is: | 1.085 FS: Suitable Dimensions
| T1 |  | Core7 |  |  | (Metering)
0
[6 empty] | Tap-1 | 1.085 FS: Tap-2; 1.085 PE: Tap-3
| CT Ratio: |  |  |  |  | 2000 | 1.085 FS: -; 1.085 PE: -; 1.085 PN: /; 1.085 ) / (: 1; 1.085 PE: A
| Class of Accuracy: | [5 empty] | 1.085 PE: 0.2S
| CT Resistance: | [5 empty] | 1.085 x ( (: Rct<; 1.085 PE: -; 1.085 PN: W
| Factor of Safety | [18 empty] | #VALUE! | bar: 1.085 x ( ( to 1.085 +
| Rated Burden | [5 empty] | 1.085 x ( (: PN; 1.085 PE: -; 1.085 PN: VA
Other Burdens on same CT core:
| Burden of |  | XC-RACK |  |  |  | = =: =; 1.085 FS: 0.008; 1.085 PE: VA; 1.085 PN: CT internal Burden
| Burden of |  | 0 |  |  |  | = =: =; 1.085 FS: 0; 1.085 PE: VA
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  | = | 0 |  | VA |  |  | = | 1 | x | 1 | x | -
| Total lead burden | [5 empty] | = =: =; 1.085 FS: 1.077; 1.085 PE: VA; 1.085 ) / (: =; 1.085 PE: #VALUE!; 1.085 PL: VA
| Total lead + other burden |  |  |  |  | PL | = =: =; 1.085 FS: 1.085; 1.085 PE: VA
|  | Minimum Safety Factor among all connected devices |  |  |  |  | 1.085 +: Fs(min); 1.085 PL: =; 1.085 ): 20
|  | Total connected burden on CT |  |  |  |  | = =: =; 1.085 FS: CT Int. Burden; 1.085 +: +; 1.085 PN: Connected Burden
[7 empty] | = | #VALUE! |  | + | 1.085
[7 empty] | = | #VALUE!
[6 empty] | Effective Safety Factor of CT, FS' | = | FS | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[7 empty] | = | - | x ( ( | #VALUE! | + | - | ) / ( | #VALUE! | + | 1.085 | )
[7 empty] | = | #VALUE!
CT is considered to be properly sized if following conditions are satisfied…
| 1 |  |  |  |  | Rated CT Burden | = =: >; #VALUE! FS: Total Connected Burden; #VALUE! ): …cond.1
[5 empty] | - |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
| 2 |  |  |  |  | FS(min) of connected devices | = =: >; #VALUE! FS: Effective Safety Factor of CT, FS'; #VALUE! ): …cond.2
[5 empty] | 20 |  | = =: #VALUE!; #VALUE! FS: #VALUE!; #VALUE! ): #VALUE!
[6 empty] | Hence CT is: | #VALUE! FS: #VALUE!
ABB
Summary of available CT parameters and its suitability
CT / Core |  |  | Ratio (A) |  | CT Cable m/mm2 |  | = =: Class; #VALUE! x ( (: CT Resistance (W) @ 75OC; #VALUE! +: Rated Burden VA; #VALUE! +: Relay / Instrument Type; #VALUE! ): CT Suitability
T1 | Core7 |  | 2000 | 1 | 120 | 6 | = =: 0.2S; #VALUE! x ( (: 5; #VALUE! +: 10; #VALUE! ) / (: -; #VALUE! +: XC-RACK; #VALUE! ): Not suitable
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )
- | bar: #VALUE! x ( (; #VALUE! +; #VALUE! ) / (; #VALUE! )

## VT ADEQUACY (hidden)
VT ADEQUACY CHECK
Back to
INDEX

## VT BAY1 (hidden)
HVDC FEEDER (02, 03)
Back to
INDEX

## HVDC FEEDER (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | HVDC FEEDER | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core1
| VT Ratio | [5 empty] | 400 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.5/3P
| Rated Burden | [5 empty] | 50 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | RED670 |  |  |  |  | = | 0.02 |  | VA
|  | Burden of |  | P545 |  |  |  |  | = | 0.02 |  | VA | [6 empty] | Burden of | REL670 |  | = | 0 | VA
|  | Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA | [6 empty] | Burden of | FMS |  | = | 0 | VA
|  | Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA | [6 empty] | Burden of | Synchrocheck relay | ** | = | 0.2 | VA
|  | Burden of |  | IDM+9 |  |  |  |  | = | 0.058 |  | VA
|  | Burden of |  | REB500 |  |  |  |  | = | 0.01 |  | VA | [6 empty] | Burden of | Metering + Margin | ** | = | 1 | VA
|  | Burden of |  | P743 |  |  |  |  | = | 0.1
|  | Total connected burden | [6 empty] | = | 0.248 |  | VA
|  | Total lead burden | [6 empty] | = | 2.7035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 2.9515 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 0.248 |  | / | 63.5085
[9 empty] | = | 0.003905 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 1.5249e-05 |  | x | 2.7035
[9 empty] | = | 4.1225e-05 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 50 |  | > | 2.9515
|  |  |  | Hence VT is: |  | Suitably Dimensioned
| T1 |  | Core2
| VT Ratio | [5 empty] | 400 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.2
| Rated Burden | [5 empty] | 50 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | XC-RACK |  |  |  |  | = | 0.008 |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of |  | ZIV | [7 empty] | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Total connected burden | [6 empty] | = | 0.008 |  | VA
|  | Total lead burden | [6 empty] | = | 2.7035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 2.7115 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 0.008 |  | / | 63.5085
[9 empty] | = | 0.00012597 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 1.5868e-08 |  | x | 2.7035
[9 empty] | = | 4.2899e-08 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 50 |  | > | 2.7115
|  |  |  | Hence VT is: |  | Suitably Dimensioned
| T1 |  | Core3
| VT Ratio | [5 empty] | 400 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.2
| Rated Burden | [5 empty] | 50 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | XC-RACK |  |  |  |  | = | 0.008 |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Total connected burden | [6 empty] | = | 0.008 |  | VA
|  | Total lead burden | [6 empty] | = | 2.7035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 2.7115 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 0.008 |  | / | 63.5085
[9 empty] | = | 0.00012597 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 1.5868e-08 |  | x | 2.7035
[9 empty] | = | 4.2899e-08 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 50 |  | > | 2.7115
|  |  |  | Hence VT is: |  | Suitably Dimensioned
Summary of available VT parameters and its suitability
VT / Core |  |  |  | Voltage Ratio (kV) |  |  |  |  | VT Cable m/mm2 |  | Class |  | Rated Burden (VA) |  |  | Remarks
T1 |  | Core1 |  | 400 | / √3 | / | 0.11 | / √3 | 150 | 2.5 | 0.5/3P |  | 50 |  |  | Suitably Dimensioned
|  | Core2 |  | 400 | / √3 | / | 0.11 | / √3 |  |  | 0.2 |  | 50 |  |  | Suitably Dimensioned
|  | Core3 |  | 400 | / √3 | / | 0.11 | / √3 |  |  | 0.2 |  | 50 |  |  | Suitably Dimensioned
Back to
INDEX

## VT BAY2 (hidden)
FEEDER (09, 05, 04, 08)
Back to
INDEX

## FEEDER (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | FEEDER | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core1
| VT Ratio | [5 empty] | 400 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.5/3P
| Rated Burden | [5 empty] | 50 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | RED670 |  |  |  |  | = | 0.02 |  | VA
|  | Burden of |  | P545 |  |  |  |  | = | 0.02 |  | VA | [6 empty] | Burden of | REL670 |  | = | 0 | VA
|  | Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA | [6 empty] | Burden of | FMS |  | = | 0 | VA
|  | Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA | [6 empty] | Burden of | Synchrocheck relay | ** | = | 0.2 | VA
|  | Burden of |  | IDM+9 | [5 empty] | 0.058 |  | VA
|  | Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA | [6 empty] | Burden of | Metering + Margin | ** | = | 1 | VA
|  | Burden of |  | REB500 | [5 empty] | 0.01
|  | Burden of |  | P743 | [5 empty] | 0.1
|  | Total connected burden | [6 empty] | = | 0.268 |  | VA
|  | Total lead burden | [6 empty] | = | 2.7035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 2.9715 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 0.268 |  | / | 63.5085
[9 empty] | = | 0.0042199 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 1.7808e-05 |  | x | 2.7035
[9 empty] | = | 4.8143e-05 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 50 |  | > | 2.9715
|  |  |  | Hence VT is: |  | Suitably Dimensioned
| T1 |  | Core2
| VT Ratio | [5 empty] | 400 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.2S
| Rated Burden | [5 empty] | 50 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | XC-RACK |  |  |  |  | = | 0.008 |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of |  | ZIV | [7 empty] | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Total connected burden | [6 empty] | = | 0.008 |  | VA
|  | Total lead burden | [6 empty] | = | 2.7035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 2.7115 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 0.008 |  | / | 63.5085
[9 empty] | = | 0.00012597 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 1.5868e-08 |  | x | 2.7035
[9 empty] | = | 4.2899e-08 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 50 |  | > | 2.7115
|  |  |  | Hence VT is: |  | Suitably Dimensioned
| T1 |  | Core3
| VT Ratio | [5 empty] | 400 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.2S
| Rated Burden | [5 empty] | 50 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | XC-RACK |  |  |  |  | = | 0.008 |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Total connected burden | [6 empty] | = | 0.008 |  | VA
|  | Total lead burden | [6 empty] | = | 2.7035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 2.7115 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 0.008 |  | / | 63.5085
[9 empty] | = | 0.00012597 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 1.5868e-08 |  | x | 2.7035
[9 empty] | = | 4.2899e-08 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 50 |  | > | 2.7115
|  |  |  | Hence VT is: |  | Suitably Dimensioned
Summary of available VT parameters and its suitability
VT / Core |  |  |  | Voltage Ratio (kV) |  |  |  |  | VT Cable m/mm2 |  | Class |  | Rated Burden (VA) |  |  | Remarks
T1 |  | Core1 |  | 400 | / √3 | / | 0.11 | / √3 | 150 | 2.5 | 0.5/3P |  | 50 |  |  | Suitably Dimensioned
|  | Core2 |  | 400 | / √3 | / | 0.11 | / √3 |  |  | 0.2S |  | 50 |  |  | Suitably Dimensioned
|  | Core3 |  | 400 | / √3 | / | 0.11 | / √3 |  |  | 0.2S |  | 50 |  |  | Suitably Dimensioned
Back to
INDEX

## VT BAY3 (hidden)
SGT 1, 2 & 3 (11, 07,06)
Back to
INDEX

## SGT (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | SGT 1, 2 & 3 | [6 empty] | Contractor |  |  | HITACHI
| T1 |  | Core1
| VT Ratio | [5 empty] | 400 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 3P
| Rated Burden | [5 empty] | 50 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA
|  | Burden of |  | MFAC+MVTP |  |  |  |  | = |  |  | VA | [6 empty] | Burden of | REL670 |  | = | 0 | VA
|  | Burden of |  | REF650 |  |  |  |  | = | 0.02 |  | VA | [6 empty] | Burden of | FMS |  | = | 0 | VA
|  | Burden of |  | P141 |  |  |  |  | = | 0.04 |  | VA | [6 empty] | Burden of | Synchrocheck relay | ** | = | 0.2 | VA
|  | Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA
|  | Burden of |  | IDM+19 |  |  |  |  | = | 0.058 |  | VA | [6 empty] | Burden of | Metering + Margin | ** | = | 1 | VA
|  | Burden of |  | PQ100+PM7500
|  | Burden of |  | REB500 | [5 empty] | 0.01
|  | Burden of |  | P743 | [5 empty] | 0.1
|  | Total connected burden | [6 empty] | = | 0.268 |  | VA
|  | Total lead burden | [6 empty] | = | 2.7035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 2.9715 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 0.268 |  | / | 63.5085
[9 empty] | = | 0.0042199 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 1.7808e-05 |  | x | 2.7035
[9 empty] | = | 4.8143e-05 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 50 |  | > | 2.9715
|  |  |  | Hence VT is: |  | Suitably Dimensioned
| T1 |  | Core2
| VT Ratio | [5 empty] | 33 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.2
| Rated Burden | [5 empty] | 10 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | FMS |  |  |  |  | = | 0.008 |  | VA
|  | Burden of |  | Pointer Voltmeter |  |  |  |  | = | 3.75 |  | VA
|  | Burden of |  | AVR |  |  |  |  | = |  |  | VA
|  | Burden of |  | FMS |  |  |  |  | = |  |  | VA
|  | Burden of |  | REU615 |  |  |  |  | = |  |  | VA
|  | Burden of |  | REC670 |  |  |  |  | = |  |  | VA
|  | Burden of |  | REF615 | [7 empty] | VA
|  | Burden of |  | ZIV | [7 empty] | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Total connected burden | [6 empty] | = | 3.758 |  | VA
|  | Total lead burden | [6 empty] | = | 2.7035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 6.4615 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 3.758 |  | / | 63.5085
[9 empty] | = | 0.059173 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 0.0035015 |  | x | 2.7035
[9 empty] | = | 0.0094662 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 10 |  | > | 6.4615
|  |  |  | Hence VT is: |  | Suitably Dimensioned
| VT Ratio | [7 empty] | / |  |  | kV
Class of Accuracy
| Rated Burden | [7 empty] | VA | [8 empty] | #DIV/0!
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = | 4 |  | VA
|  | Total connected burden | [6 empty] | = | 4 |  | VA
|  | Total lead burden | [6 empty] | = | #DIV/0! |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | #DIV/0! |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 4 |  | / | 0
[9 empty] | = | #DIV/0! |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | #DIV/0! |  | x | 2.7035
[9 empty] | = | #DIV/0! |  | VA
The criteria is:
|  |  |  | Proposed VA | #DIV/0! | Required VA
|  |  | 0 |  | #DIV/0! | #DIV/0!
|  |  |  | Hence VT is: |  | #DIV/0!
Summary of available VT parameters and its suitability
VT / Core |  |  |  | Voltage Ratio (kV) |  |  |  |  | VT Cable m/mm2 |  | Class |  | Rated Burden (VA) |  |  | Remarks
T1 |  | Core1 |  | 400 | / √3 | / | 0.11 | / √3 | 150 | 2.5 | 3P |  | 50 |  |  | Suitably Dimensioned
|  | - |  | - |  | - | - |  |  |  | - |  | - |  |  | -
|  | - |  | - |  | - | - |  |  |  | - |  | - |  |  | -
Back to
INDEX

## Bus VT (2) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV BUS VT | [6 empty] | Contractor |  |  | HITACHI
| T15/T25 |  | Core1
T16/T26
T17/T27
| VT Ratio | [5 empty] | 33 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.2
| Rated Burden | [5 empty] | 100 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | Main Tariff Meter |  |  |  |  | = | 27 |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Total connected burden | [6 empty] | = | 27 |  | VA
|  | Total lead burden | [6 empty] | = | 27.035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 54.035 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 27 |  | / | 63.5085
[9 empty] | = | 0.42514 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 0.18074 |  | x | 2.7035
[9 empty] | = | 0.48864 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 100 |  | > | 54.035
|  |  |  | Hence VT is: |  | Suitably Dimensioned
| T15/T25 |  | Core2
T16/T26
T17/T27
| VT Ratio | [5 empty] | 33 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.2/3P
| Rated Burden | [5 empty] | 100 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | Check Tariff Meter |  |  |  |  | = | 27 |  | VA
|  | Burden of |  | Voltmeter |  |  |  |  | = | 3.75 |  | VA
|  | Burden of |  | OV/UV |  |  |  |  | = | 0.1 |  | VA
|  | Burden of |  | UF Load Shed. |  |  |  |  | = | 0.02 |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Total connected burden | [6 empty] | = | 30.87 |  | VA
|  | Total lead burden | [6 empty] | = | 27.035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 57.905 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 30.87 |  | / | 63.5085
[9 empty] | = | 0.48608 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 0.23627 |  | x | 2.7035
[9 empty] | = | 0.63876 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 100 |  | > | 57.905
|  |  |  | Hence VT is: |  | Suitably Dimensioned
| T15/T25 |  | Core3
T16/T26
T17/T27
| VT Ratio | [5 empty] | 33 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.2/3P
| Rated Burden | [5 empty] | 100 |  | VA | [8 empty] | Suitably Dimensioned
|  | Burden of |  | SEL751 |  |  |  |  | = | 1.2 |  | VA
|  | Burden of |  | IDM |  |  |  |  | = | 0.756 |  | VA
|  | Burden of |  | 7SJ85 |  |  |  |  | = | 1.6 |  | VA
|  | Burden of |  | 87C |  |  |  |  | = | 0.24 |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Total connected burden | [6 empty] | = | 3.796 |  | VA
|  | Total lead burden | [6 empty] | = | 27.035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 30.831 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 3.796 |  | / | 63.5085
[9 empty] | = | 0.059771 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 0.0035726 |  | x | 2.7035
[9 empty] | = | 0.0096586 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 100 |  | > | 30.831
|  |  |  | Hence VT is: |  | Suitably Dimensioned
Hence, the Recommended VT Parameters for Manufacturing are:
VT / Core |  |  |  | Voltage Ratio (kV) |  |  |  |  | VT Cable m/mm2 |  | Class |  | Rated Burden (VA) |  |  | Remarks
T15/T25,T16/T26,T17/T27 |  | Core1 |  | 33 | / √3 | / | 0.11 | / √3 | 150 | 2.5 | 0.2 |  | 100 |  |  | Suitably Dimensioned
|  | Core2 |  | 33 | / √3 | / | 0.11 | / √3 |  |  | 0.2/3P |  | 100 |  |  | Suitably Dimensioned
|  | Core3 |  | 33 | / √3 | / | 0.11 | / √3 |  |  | 0.2/3P |  | 100 |  |  | Suitably Dimensioned
Back to
INDEX

## Bus VT (3) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV BUS VT | [6 empty] | Contractor |  |  | HITACHI
| T15 |  | Core1
T16
T17
| VT Ratio | [5 empty] | 33 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.5/3P
| Rated Burden | [5 empty] | 20 |  | VA | [9 empty] | Suitably Dimensioned
|  | Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA
|  | Burden of |  | REU615 |  |  |  |  | = | 0.05 |  | VA | [7 empty] | SEL751
|  | Burden of |  | RED670 |  |  |  |  | = | 0.02 |  | VA | [7 empty] | REC670
|  | Burden of |  | REC670 |  |  |  |  | = | 0.02 |  | VA | [7 empty] | RED670
|  | Burden of | [6 empty] | = |  |  | VA
|  | Total connected burden | [6 empty] | = | 0.11 |  | VA
|  | Total lead burden | [6 empty] | = | 2.7035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 2.8135 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 0.11 |  | / | 63.5085
[9 empty] | = | 0.0017321 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 3e-06 |  | x | 2.7035
[9 empty] | = | 8.1105e-06 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 20 |  | > | 2.8135
|  |  |  | Hence VT is: |  | Suitably Dimensioned
| T15 |  | Core2
T16
T17
| VT Ratio | [5 empty] | 33 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 0.2
| Rated Burden | [5 empty] | 10 |  | VA | [9 empty] | Suitably Dimensioned
|  | Burden of |  | Pointer Voltmeter |  |  |  |  | = | 3.75 |  | VA
|  | Burden of |  | FMS |  |  |  |  | = | 0.378 |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | =
|  | Total connected burden | [6 empty] | = | 4.128 |  | VA
|  | Total lead burden | [6 empty] | = | 2.7035 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 6.8315 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 4.128 |  | / | 63.5085
[9 empty] | = | 0.064999 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 0.0042249 |  | x | 2.7035
[9 empty] | = | 0.011422 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 10 |  | > | 6.8315
|  |  |  | Hence VT is: |  | Suitably Dimensioned
| VT |  | Core3
| VT Ratio | [5 empty] | 33 | / √3 | / | 0.11 | / √3 | kV
| Class of Accuracy | [5 empty] | 3P
| Rated Burden | [5 empty] | 50 |  | VA | [9 empty] | Suitably Dimensioned
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = |  |  | VA
|  | Burden of | [6 empty] | = | 4 |  | VA
|  | Total connected burden | [6 empty] | = | 4 |  | VA
|  | Total lead burden | [6 empty] | = | 0.010725 |  | VA
|  | Total lead + other burden | [5 empty] | PL | = | 4.0107 |  | VA
Burden of connecting leads:
| Secondary Current, Is | [7 empty] | = | Total connected burden |  |  |  |  | / | Voltage
[9 empty] | = | 4 |  | / | 63.5085
[9 empty] | = | 0.062984 |  | A
| VA Consumption of the connecting leads | [7 empty] | = | Is2 |  | x | Lead resistance
[9 empty] | = | 0.0039669 |  | x | 2.7035
[9 empty] | = | 0.010725 |  | VA
The criteria is:
|  |  |  | Proposed VA | > | Required VA
|  |  | 50 |  | > | 4.0107
|  |  |  | Hence VT is: |  | Suitably Dimensioned
ABB
Hence, the Recommended VT Parameters for Manufacturing are:
VT / Core |  |  |  | Voltage Ratio (kV) |  |  |  |  | VT Cable m/mm2 |  | Class |  | Rated Burden (VA) |  |  | Remarks
T15,T16,T17 |  | Core1 |  | 33 | / √3 | / | 0.11 | / √3 | 150 | 2.5 | 0.5/3P |  | 20 |  |  | Suitably Dimensioned
|  | Core2 |  | 33 | / √3 | / | 0.11 | / √3 |  |  | 0.2 |  | 10 |  |  | Suitably Dimensioned
Back to
INDEX

## P54x-X-3 (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2025-09-25
[7 empty] | 33kV DF5W SS | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV CABLE FEEDERS | [6 empty] | Contractor |  |  | HITACHI
| CT7001 |  | Core2 |  | Main-2 |  | (Differential + Distance) | [10 empty] | Connected devices: | P545
| CT7004 |  | Core5
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 4000 |  | 3000 |  | - |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX
| CT Resistance: |  |  |  |  | Rct< | 14 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 4000 |  | V | [12 empty] | Highest Vk required = | 2930.2613
| Magnetizing Current: |  |  |  |  | I0< | 25 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | P545 |  |  |  | Sr' | = | 0.02 |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Burden of |  | 0 |  |  |  |  | = |  |  | VA
| Total lead burden | [6 empty] | = | 0.56186 |  | VA
| Total lead + other burden | [5 empty] | Sl | = | 0.56186 |  | VA
| Resisitance of the relay: | [10 empty] | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.02 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 0.56186 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.02; Resisitance of the relay: Ir: W |  |  |  |  | = | 0.56186 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, 2Rl |  |  | = | 0.02 |  | + | 0.56186 |  | = | 0.58186 |  | W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The knee point voltage of the CTs should comply with the minimum requirements of the formulae shown below:
| Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | ) | [9 empty] | …1
A constant depending on the maximum value of through fault current, If (as a multiple of In) and the primary system X/R ratio. K is determined as follows:
1 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 150% (k2 typically set at 150% for two-ended current differential schemes):
| When | ( | if |  | x | X/R | ) | ≤ | ( | 1000 | x | In | ) | [6 empty] | ...cond.1
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.07 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 1000 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 2600 | x | In | ) | …cond.2
| K | = | 107
2 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 100% (k2 typically set at 100% for tapped lines)
| When | ( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [6 empty] | ...cond.3
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) | …cond.4
| K | = | 256
| Resisitance of the relay: Rr: Maximum through fault current | [7 empty] | If |  | = | 55677 |  | A
| Resisitance of the relay: Rr: CT Primary Current | [7 empty] | Ipn |  | = | 4000 |  | A
| Resisitance of the relay: Rr: Maximum through fault current (referred to secondary) | [7 empty] | if |  | = | 13.9192 |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [7 empty] | Rct |  | = | 14 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [7 empty] | 2Rl |  | = | 0.58186 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [7 empty] | In |  | = | 1 |  | A
| Resisitance of the relay: Rr: Primary X/R ratio | [7 empty] | X/R |  | = | 23.6
| Resisitance of the relay: Rr: Enter the setting K2: | [10 empty] | 100 |  | %
| Checking condition |  |  |  | 3 & 4
( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [8 empty] | …cond.3
( | 13.9192 |  | x | 23.6 | ) | ≤ | ( | 600 | x | 1 | )
| Resisitance of the relay: Sr': 328.4943; Resisitance of the relay: x: ≤; Resisitance of the relay: ): 600 | [9 empty] | … | TRUE
| If | …cond.3 |  | is TRUE, the value of K must be highest of:
|  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | ) |  | Hence K |  | = | 154.973
|  |  | ≥ | 40 | + | 0.35 | x ( | 13.9192 |  | x | 23.6 | )
|  |  | ≥ | 154.973
| OR | K | = | 65
( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) |  |  | …cond.4
( | 600 | x | 1 | ) | < | ( | 13.9192 |  | x | 23.6 | ) | ≤ | ( | 1600 | x | 1 | )
| Resisitance of the relay: =: 600; Resisitance of the relay: Ir: <; Resisitance of the relay: ): 328.4943 |  |  |  | ≤ |  | 1600 |  |  |  | … | FALSE
| Resisitance of the relay: Rr: If; Resisitance of the relay: =: …cond.4; Resisitance of the relay: / (: is TRUE, the value of K | = | 256 |  |  | Hence, final value of K |  |  |  |  | = | 154.973
Hence, Vk required for Diff. function:
|  |  | Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | )
|  |  |  | ≥ | 154.973 | x | 1 | x ( | 14 | + | 0.58186 | )
|  |  |  | ≥ | 2259.7949 |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
For Close-in faults:
The calculation must be performed for all cables and lines where the source impedance ratio (SIR) may be less than SIR = 2.
| Resisitance of the relay: Ir: SIR; Resisitance of the relay: x: =; Resisitance of the relay: Ir: 44.6498 |  | Since SIR is >2, the below calculation is not applicable
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: x: Kmax; Resisitance of the relay: ): = | Fixed Dimentioning Factory = always 1.4 | [8 empty] | = | 1.4
| Resisitance of the relay: x: Ifmax; Resisitance of the relay: ): = | Max secondary phase-fault current | [8 empty] | = | 13.9192 |  | A
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 1.4 | x | 13.9192 |  | x | ( | 14 | + | 0.58186 | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 284.156 | Volts
Zone-1 reach point accuracy (RPA):
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: Sr': KRPA; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Fixed Dimentioning Factory = always 0.6 | [9 empty] | = | 0.6
| Resisitance of the relay: Sr': IFZ1; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Max secondary phase-fault current at Zone 1 reach point | [9 empty] | = | 13.6147 |  | A
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
|  | Vk | ≥ | 0.6 |  | x | 13.6147 |  | x ( | 1 | + | 23.6 | ) x ( | 14 | + | 0.58186 | )
|  | Vk | ≥ | 2930.2613 |  | Volts
| Resisitance of the relay: Rr: Hence, highest Vk required for Diff. & Dist. Functions: |  |  |  | 2930.2613 |  | Volts
|  | Available Vk |  |  | > | Required Vk
|  |  | 4000 |  | > | 2930.2613
|  |  |  | Hence CT is: |  | Suitably Dimensioned
| Resisitance of the relay: Rr: CT7001; Resisitance of the relay: Sr': Core2; Resisitance of the relay: Ir: Main-2; Resisitance of the relay: Ir: (Differential + Distance) | [9 empty] | Connected devices: | P545
| Resisitance of the relay: Rr: CT7004; Resisitance of the relay: Sr': Core5 | [10 empty] | 0
| Resisitance of the relay: Ir: Tap-1 | Tap-2 |  | Tap-3 | [7 empty] | 0
| Resisitance of the relay: Rr: CT Ratio:; Resisitance of the relay: Ir: 4000 | 3000 |  | - |  | / | 1 | A
| Resisitance of the relay: Rr: Class of Accuracy: | PX
| Resisitance of the relay: Rr: CT Resistance:; Resisitance of the relay: ): Rct< | 10 |  | W
| Resisitance of the relay: Rr: Knee Point Voltage:; Resisitance of the relay: ): Vk> | 3000 |  | V | [10 empty] | Highest Vk required = | 2835.2684
| Resisitance of the relay: Rr: Magnetizing Current:; Resisitance of the relay: ): I0< | 30 |  | mA at Vk
Other Burdens on same CT core:
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': P545; Resisitance of the relay: Ir: Sr'; Resisitance of the relay: ): = | 0.02 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Total lead burden; Resisitance of the relay: ): = | 0.56186 |  | VA
| Resisitance of the relay: Rr: Total lead + other burden; Resisitance of the relay: Ir: Sl; Resisitance of the relay: ): = | 0.56186 |  | VA
| Resisitance of the relay: Rr: Resisitance of the relay: |  |  |  | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.02 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 0.56186 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.02; Resisitance of the relay: Ir: W |  |  |  |  | = | 0.56186 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, 2Rl |  |  | = | 0.02 |  | + | 0.56186 |  | = | 0.58186 |  | W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The knee point voltage of the CTs should comply with the minimum requirements of the formulae shown below:
| Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | ) | [9 empty] | …1
A constant depending on the maximum value of through fault current, If (as a multiple of In) and the primary system X/R ratio. K is determined as follows:
1 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 150% (k2 typically set at 150% for two-ended current differential schemes):
| When | ( | if |  | x | X/R | ) | ≤ | ( | 1000 | x | In | ) | [6 empty] | ...cond.1
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.07 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 1000 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 2600 | x | In | ) | …cond.2
| K | = | 107
2 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 100% (k2 typically set at 100% for tapped lines)
| When | ( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [6 empty] | ...cond.3
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) | …cond.4
| K | = | 256
| Resisitance of the relay: Rr: Maximum through fault current | [7 empty] | If |  | = | 55677 |  | A
| Resisitance of the relay: Rr: CT Primary Current | [7 empty] | Ipn |  | = | 3000 |  | A
| Resisitance of the relay: Rr: Maximum through fault current (referred to secondary) | [7 empty] | if |  | = | 18.559 |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [7 empty] | Rct |  | = | 10 |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [7 empty] | 2Rl |  | = | 0.58186 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [7 empty] | In |  | = | 1 |  | A
| Resisitance of the relay: Rr: Primary X/R ratio | [7 empty] | X/R |  | = | 23.6
| Resisitance of the relay: Rr: Enter the setting K2: | [10 empty] | 100 |  | %
| Checking condition |  |  |  | 3 & 4
( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [8 empty] | …cond.3
( | 18.559 |  | x | 23.6 | ) | ≤ | ( | 600 | x | 1 | )
| Resisitance of the relay: Sr': 437.9924; Resisitance of the relay: x: ≤; Resisitance of the relay: ): 600 | [9 empty] | … | TRUE
| If | …cond.3 |  | is TRUE, the value of K must be highest of:
|  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | ) |  | Hence K |  | = | 193.2973
|  |  | ≥ | 40 | + | 0.35 | x ( | 18.559 |  | x | 23.6 | )
|  |  | ≥ | 193.2973
| OR | K | = | 65
( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) |  |  | …cond.4
( | 600 | x | 1 | ) | < | ( | 18.559 |  | x | 23.6 | ) | ≤ | ( | 1600 | x | 1 | )
| Resisitance of the relay: =: 600; Resisitance of the relay: Ir: <; Resisitance of the relay: ): 437.9924 |  |  |  | ≤ |  | 1600 |  |  |  | … | FALSE
| Resisitance of the relay: Rr: If; Resisitance of the relay: =: …cond.4; Resisitance of the relay: / (: is TRUE, the value of K | = | 256 |  |  | Hence, final value of K |  |  |  |  | = | 193.2973
Hence, Vk required for Diff. function:
|  |  | Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | )
|  |  |  | ≥ | 193.2973 | x | 1 | x ( | 10 | + | 0.58186 | )
|  |  |  | ≥ | 2045.4456 |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
For Close-in faults:
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: x: Kmax; Resisitance of the relay: ): = | Fixed Dimentioning Factory = always 1.4 | [8 empty] | = | 1.4
| Resisitance of the relay: x: Ifmax; Resisitance of the relay: ): = | Max secondary phase-fault current | [8 empty] | = | 18.559 |  | A
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 1.4 | x | 18.559 |  | x | ( | 10 | + | 0.58186 | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 274.9443 | Volts
Zone-1 reach point accuracy (RPA):
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: Sr': KRPA; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Fixed Dimentioning Factory = always 0.6 | [9 empty] | = | 0.6
| Resisitance of the relay: Sr': IFZ1; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Max secondary phase-fault current at Zone 1 reach point | [9 empty] | = | 18.1529 |  | A
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
|  | Vk | ≥ | 0.6 |  | x | 18.1529 |  | x ( | 1 | + | 23.6 | ) x ( | 10 | + | 0.58186 | )
|  | Vk | ≥ | 2835.2684 |  | Volts
| Resisitance of the relay: Rr: Hence, highest Vk required for Diff. & Dist. Functions: |  |  |  | 2835.2684 |  | Volts
|  | Available Vk |  |  | > | Required Vk
|  |  | 3000 |  | > | 2835.2684
|  |  |  | Hence CT is: |  | Suitably Dimensioned
| Resisitance of the relay: Rr: CT7001; Resisitance of the relay: Sr': Core2; Resisitance of the relay: Ir: Main-2; Resisitance of the relay: Ir: (Differential + Distance) | [9 empty] | Connected devices: | P545
| Resisitance of the relay: Rr: CT7004 | [10 empty] | 0
| Resisitance of the relay: Ir: Tap-1 | Tap-2 |  | Tap-3 | [7 empty] | 0
| Resisitance of the relay: Rr: CT Ratio:; Resisitance of the relay: Ir: 4000 | 3000 |  | - |  | / | 1 | A
| Resisitance of the relay: Rr: Class of Accuracy: |  |  | PX
| Resisitance of the relay: Rr: CT Resistance: |  | Rct< | - |  | W
| Resisitance of the relay: Rr: Knee Point Voltage: |  | Vk> | - |  | V | [8 empty] | Highest Vk required = | #VALUE!
| Resisitance of the relay: Rr: Magnetizing Current: |  | I0< | - |  | mA at Vk
Other Burdens on same CT core:
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': P545; Resisitance of the relay: Ir: Sr'; Resisitance of the relay: ): = | 0.02 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Burden of; Resisitance of the relay: Sr': 0; Resisitance of the relay: ): = | 0 |  | VA
| Resisitance of the relay: Rr: Total lead burden; Resisitance of the relay: ): = | 0.56186 |  | VA
| Resisitance of the relay: Rr: Total lead + other burden; Resisitance of the relay: Ir: Sl; Resisitance of the relay: ): = | 0.56186 |  | VA
| Resisitance of the relay: Rr: Resisitance of the relay: |  |  |  | Lead + Other resisitance connected
| Rr | = | Sr' | / ( | Ir | x | Ir | ) |  |  |  | Rl | = | Sl | / ( | Isn | x | Isn | )
|  | = | 0.02 | / ( | 1 | x | 1 | ) |  |  |  |  | = | 0.56186 | / ( | 1 | x | 1 | )
| Resisitance of the relay: =: =; Resisitance of the relay: Sr': 0.02; Resisitance of the relay: Ir: W |  |  |  |  | = | 0.56186 |  | W
| Resisitance of the relay: Rr: Hence, Total Burden connected to CT core, 2Rl |  |  | = | 0.02 | + | 0.56186 | = | 0.58186 | W
A. CT ADEQUECY CHECK FOR DIFFERENTIAL FUNCTION:
The knee point voltage of the CTs should comply with the minimum requirements of the formulae shown below:
| Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | ) | [9 empty] | …1
A constant depending on the maximum value of through fault current, If (as a multiple of In) and the primary system X/R ratio. K is determined as follows:
1 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 150% (k2 typically set at 150% for two-ended current differential schemes):
| When | ( | if |  | x | X/R | ) | ≤ | ( | 1000 | x | In | ) | [6 empty] | ...cond.1
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.07 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 1000 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 2600 | x | In | ) | …cond.2
| K | = | 107
2 | Resisitance of the relay: Rr: For relays set at Is1 = 0.2In, k1 = 30%, Is2 = 2In, k2 = 100% (k2 typically set at 100% for tapped lines)
| When | ( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [6 empty] | ...cond.3
K must be highest of:
|  |  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | )
|  | OR | K | ≥ | 65
| When | ( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) | …cond.4
| K | = | 256
| Resisitance of the relay: Rr: Maximum through fault current | [7 empty] | If |  | = | 55677 |  | A
| Resisitance of the relay: Rr: CT Primary Current | [7 empty] | Ipn |  | = | - |  | A
| Resisitance of the relay: Rr: Maximum through fault current (referred to secondary) | [7 empty] | if |  | = | #VALUE! |  | A
| Resisitance of the relay: Rr: CT Internal Resistance | [7 empty] | Rct |  | = | - |  | W
| Resisitance of the relay: Rr: Burden of CT Leads and burden of relay | [7 empty] | 2Rl |  | = | 0.58186 |  | W
| Resisitance of the relay: Rr: Rated CT Secondary Current | [7 empty] | In |  | = | 1 |  | A
| Resisitance of the relay: Rr: Primary X/R ratio | [7 empty] | X/R |  | = | 23.6
| Resisitance of the relay: Rr: Enter the setting K2: | [10 empty] | 100 |  | %
| Checking condition |  |  |  | 3 & 4
( | if |  | x | X/R | ) | ≤ | ( | 600 | x | In | ) | [8 empty] | …cond.3
( | #VALUE! |  | x | 23.6 | ) | ≤ | ( | 600 | x | 1 | )
| Resisitance of the relay: Sr': #VALUE!; Resisitance of the relay: x: ≤; Resisitance of the relay: ): 600 | [9 empty] | … | #VALUE!
| If | …cond.3 |  | is TRUE, the value of K must be highest of:
|  | K | ≥ | 40 | + | 0.35 | x ( | if |  | x | X/R | ) |  | Hence K |  | = | #VALUE!
|  |  | ≥ | 40 | + | 0.35 | x ( | #VALUE! |  | x | 23.6 | )
|  |  | ≥ | #VALUE!
| OR | K | = | 65
( | 600 | x | In | ) | < | ( | if |  | x | X/R | ) | ≤ | ( | 1600 | x | In | ) |  |  | …cond.4
( | 600 | x | 1 | ) | < | ( | #VALUE! |  | x | 23.6 | ) | ≤ | ( | 1600 | x | 1 | )
| Resisitance of the relay: =: 600; Resisitance of the relay: Ir: <; Resisitance of the relay: ): #VALUE! |  |  |  | ≤ |  | 1600 |  |  |  | … | #VALUE!
| Resisitance of the relay: Rr: If; Resisitance of the relay: =: …cond.4; Resisitance of the relay: / (: is TRUE, the value of K | = | 256 |  |  | Hence, final value of K |  |  |  |  | = | #VALUE!
Hence, Vk required for Diff. function:
|  |  | Vk | ≥ | K | x | In | x ( | Rct | + | 2Rl | )
|  |  |  | ≥ | #VALUE! | x | 1 | x ( | - | + | 0.58186 | )
|  |  |  | ≥ | #VALUE! |  | V
B. CT ADEQUECY CHECK FOR DISTANCE FUNCTION:
For Close-in faults:
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: x: Kmax; Resisitance of the relay: ): = | Fixed Dimentioning Factory = always 1.4 | [8 empty] | = | 1.4
| Resisitance of the relay: x: Ifmax; Resisitance of the relay: ): = | Max secondary phase-fault current | [8 empty] | = | #VALUE! |  | A
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: Kmax | x | Ifmax |  | x | ( | Rct | + | Rl | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: 1.4 | x | #VALUE! |  | x | ( | - | + | 0.58186 | )
| Resisitance of the relay: Ir: Vk; Resisitance of the relay: x: ≥; Resisitance of the relay: Ir: #VALUE! | Volts
Zone-1 reach point accuracy (RPA):
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
Where:
| Resisitance of the relay: Sr': KRPA; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Fixed Dimentioning Factory = always 0.6 | [9 empty] | = | 0.6
| Resisitance of the relay: Sr': IFZ1; Resisitance of the relay: Ir: =; Resisitance of the relay: x: Max secondary phase-fault current at Zone 1 reach point | [9 empty] | = | #VALUE! |  | A
|  | Vk | ≥ | KRPA |  | x | IFZ1 |  | x ( | 1 | + | X/R | ) x ( | Rct | + | Rl | )
|  | Vk | ≥ | 0.6 |  | x | #VALUE! |  | x ( | 1 | + | 23.6 | ) x ( | - | + | 0.58186 | )
|  | Vk | ≥ | #VALUE! |  | Volts
| Resisitance of the relay: Rr: Hence, highest Vk required for Diff. & Dist. Functions: |  |  |  | #VALUE! |  | Volts
|  | Available Vk |  |  | #VALUE! | Required Vk
|  |  | - |  | #VALUE! | #VALUE!
|  |  |  | Hence CT is: |  | #VALUE!
Summary of CT parameters and its suitability
CT / Core | Resisitance of the relay: Sr': Ratio (A); Resisitance of the relay: x: CT Cable m/mm2; Resisitance of the relay: ): Class |  | Rct @ 75OC (Ω) |  | Rated Vk (V) |  | Im @ Vk (mA) |  | Connected Devices |  | CT Suitability
CT7001 | Core2 |  | 4000 |  | 1 | 75 | 6 | PX |  | 14 |  | 4000 |  | 25 |  | P545 |  | Suitably Dimensioned
| Resisitance of the relay: Sr': 3000 |  | 10 |  | 3000 |  | 30 |  |  |  | Suitably Dimensioned
[10 empty] | - |  | - |  | - | bar: Resisitance of the relay: Sr'
CT7004 | Core5 |  | 4000 |  | 1 | 75 | 6 | PX |  | 14 |  | 4000 |  | 25 |  | P545 |  | Suitably Dimensioned
| Resisitance of the relay: Sr': 3000 |  | 10 |  | 3000 |  | 30 |  |  |  | Suitably Dimensioned
[10 empty] | - |  | - |  | - |  |  |  | 0 | bar: Resisitance of the relay: Sr'

## OC+FMS+BFR-X (BS) (hidden)
HITACHI | [6 empty] | CT / VT | [6 empty] | Contract No. |  |  | N-19957.1-DF5W
[7 empty] | ADEQUACY CHECK | [6 empty] | Date |  |  | 2026-03-25
[7 empty] | LT14 - LEWIS 400/132kV SUBSTATION | [6 empty] | Document No. |  |  | -
[14 empty] | Revision No. |  |  | A
Prep. By |  | AP | Checked By |  |  | RB | 33kV CABLE FEEDERS | [6 empty] | Contractor |  |  | HITACHI
| CT1L |  | Core1 |  |  |  | (OC+FMS+BFR) | [10 empty] | Connected devices:
[7 empty] | Tap-1 |  | Tap-2 |  | Tap-3
| CT Ratio: | [5 empty] | 800 |  | 2000 |  | 1000 |  | / | 1 | A
| Class of Accuracy: | [5 empty] | PX
| CT Resistance: |  |  |  |  | Rct< | 2.8 |  | W
| Knee Point Voltage: |  |  |  |  | Vk> | 326 |  | V | [12 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  |  | I0< | 40 |  | mA at Vk
Other Burdens on same CT core:
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | CT internal Burden
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  | PE | = | In | x | In | x | Rct
| Burden of |  | 0 |  |  |  |  | = |  |  | VA |  |  | = | 1 | x | 1 | x | 2.8
| Total lead burden | [6 empty] | = | 0.23593 |  | VA |  |  | = | 2.8 |  | VA
| Total lead + other burden | [5 empty] | PL | = | 0.23593 |  | VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 17140 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 800 |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 326 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 2.8 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 0.23593 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 10
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | PN | = | ( ( | 1.3 | x | 326 |  | x | 1 | ) / | 10 | ) - | 2.8
|  |  | = | 39.58 |  | VA
ABB
|  |  |  | Required Kssc' | = | Itkmax |  | / | Ipn
[5 empty] | = | 17140 |  | / | 800
[5 empty] | = | 21.425
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 10 | x ( ( | 2.8 | + | 39.58 | ) / ( | 2.8 | + | 0.23593 | )
[5 empty] | = | 139.5946
|  |  |  | Available Kssc' | = =: >; 21.425 n: Required Kssc'
|  |  | 139.5946 |  | = =: >; 21.425 n: 21.425
|  |  |  | Hence CT is: | 21.425 n: Suitably Dimentioned
ABB
| CT1L |  | Core1 |  | 21.425 x ( (: (OC+FMS+BFR) |  |  | Connected devices: | 0
0
[5 empty] | 21.425 x ( (: Tap-1; 21.425 +: Tap-2; 21.425 ) / (: Tap-3 |  |  |  | 0
| CT Ratio: |  |  |  | 21.425 x ( (: 800; 21.425 +: 2000; 21.425 ) / (: 1000; 21.425 +: /; 21.425 PL: 1; 21.425 ): A
Class of Accuracy: | bar: 21.425 +
| CT Resistance: |  |  |  | 21.425 PE: Rct<; 21.425 +: 12; 21.425 ) / (: W
| Knee Point Voltage: |  |  |  | 21.425 PE: Vk>; 21.425 +: 1200; 21.425 ) / (: V | [6 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  | 21.425 PE: I0<; 21.425 +: 50; 21.425 ) / (: mA at Vk
Other Burdens on same CT core:
| Burden of |  | 0 |  | 21.425 PE: =; 21.425 +: 0; 21.425 ) / (: VA; 21.425 +: CT internal Burden
| Burden of |  | 0 |  | 21.425 PE: =; 21.425 +: 0; 21.425 ) / (: VA; 21.425 +: PE; 21.425 PL: =; 21.425 ): In | x | In | x | Rct
| Burden of |  | 0 |  | 21.425 PE: =; 21.425 +: 0; 21.425 ) / (: VA; 21.425 PL: =; 21.425 ): 1 | x | 1 | x | 12
| Total lead burden |  |  |  | 21.425 PE: =; 21.425 +: 0.23593; 21.425 ) / (: VA; 21.425 PL: =; 21.425 ): 12 |  | VA
| Total lead + other burden |  |  |  | 21.425 x ( (: PL; 21.425 PE: =; 21.425 +: 0.23593; 21.425 ) / (: VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 17140 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 2000 |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 1200 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 12 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 0.23593 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | PN | = | ( ( | 1.3 | x | 1200 |  | x | 1 | ) / | 20 | ) - | 12
|  |  | = | 66 | bar: 21.425 n
ABB
|  |  |  | Required Kssc' | = =: =; 21.425 n: Itkmax; 21.425 PE: /; 21.425 +: Ipn
[5 empty] | = | 17140 |  | / | 2000
[5 empty] | = | 8.57
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 12 | + | 66 | ) / ( | 12 | + | 0.23593 | )
[5 empty] | = | 127.4933
|  |  |  | Available Kssc' | = =: >; 8.57 n: Required Kssc'
|  |  | 127.4933 |  | = =: >; 8.57 n: 8.57
|  |  |  | Hence CT is: | 8.57 n: Suitably Dimentioned
ABB
| CT1L |  | Core1 |  | 8.57 x ( (: (OC+FMS+BFR) |  |  | Connected devices: | 0
0
[5 empty] | 8.57 x ( (: Tap-1; 8.57 +: Tap-2; 8.57 ) / (: Tap-3 |  |  |  | 0
| CT Ratio: |  |  |  | 8.57 x ( (: 800; 8.57 +: 2000; 8.57 ) / (: 1000; 8.57 +: /; 8.57 PL: 1; 8.57 ): A
Class of Accuracy: | bar: 8.57 ) / (
| CT Resistance: |  |  |  | 8.57 PN: Rct<; 8.57 ) / (: 8; 8.57 +: W
| Knee Point Voltage: |  |  |  | 8.57 PN: Vk>; 8.57 ) / (: 800; 8.57 +: V | [6 empty] | Suitably Dimentioned
| Magnetizing Current: |  |  |  | 8.57 PN: I0<; 8.57 ) / (: 75; 8.57 +: mA at Vk
Other Burdens on same CT core:
| Burden of |  | 0 |  | 8.57 PE: =; 8.57 +: 0; 8.57 ) / (: VA; 8.57 +: CT internal Burden
| Burden of |  | 0 |  | 8.57 PE: =; 8.57 +: 0; 8.57 ) / (: VA; 8.57 +: PE; 8.57 PL: =; 8.57 ): In | x | In | x | Rct
| Burden of |  | 0 |  | 8.57 PE: =; 8.57 +: 0; 8.57 ) / (: VA; 8.57 PL: =; 8.57 ): 1 | x | 1 | x | 8
| Total lead burden |  |  |  | 8.57 PE: =; 8.57 +: 0.23593; 8.57 ) / (: VA; 8.57 PL: =; 8.57 ): 8 |  | VA
| Total lead + other burden |  |  |  | 8.57 x ( (: PL; 8.57 PE: =; 8.57 +: 0.23593; 8.57 ) / (: VA
The design values according to BS can be approximately transferred in to IEC60044 Standard using the following formula:
|  | Vk | = | ( ( | PN | + | PE | ) x | n | ) / ( | In | x | 1.3 | )
Or
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | Max through fault current at close in fault | [13 empty] | Itkmax | = | 17140 |  | A
|  | CT Primary Current, | [13 empty] | Ipn | = | 1000 |  | A
|  | Rated Knee Point Voltage, | [13 empty] | Vk | = | 800 |  | V
|  | Internal Burden, | [13 empty] | PE | = | 8 |  | VA
|  | Burden of CT Leads and burden of connected devices | [13 empty] | PL | = | 0.23593 |  | VA
|  | Rated Secondary Current, | [13 empty] | In | = | 1 |  | A
|  | CT Accuracy Limiting Factor | [13 empty] | n | = | 20
|  | CT Burden | [13 empty] | PN
|  | PN | = | ( ( | 1.3 | x | Vk |  | x | In | ) / | n | ) - | PE
|  | PN | = | ( ( | 1.3 | x | 800 |  | x | 1 | ) / | 20 | ) - | 8
|  |  | = | 44 | bar: 8.57 n
ABB
|  |  |  | Required Kssc' | = =: =; 8.57 n: Itkmax; 8.57 PE: /; 8.57 +: Ipn
[5 empty] | = | 17140 |  | / | 1000
[5 empty] | = | 17.14
|  |  |  | Available (effective) Kssc' | = | n | x ( ( | PE | + | PN | ) / ( | PE | + | PL | )
[5 empty] | = | 20 | x ( ( | 8 | + | 44 | ) / ( | 8 | + | 0.23593 | )
[5 empty] | = | 126.2759
|  |  |  | Available Kssc' | = =: >; 17.14 n: Required Kssc'
|  |  | 126.2759 |  | = =: >; 17.14 n: 17.14
|  |  |  | Hence CT is: | 17.14 n: Suitably Dimentioned
ABB
Hence, the Recommended CT Parameters for Manufacturing are:
CT / Core |  |  | Ratio (A) |  | 17.14 x ( (: CT Cable m/mm2; 17.14 +: Class; 17.14 ) / (: CT Resistance (W) @ 75OC; 17.14 +: CT Resistance (W) @ 75OC; 17.14 PL: Knee point Voltage (Vk), V |  | Mag. Current (Io), mA at Vk |  |  | Relay / Instrument Type
CT1L | CT1L | Core1 | 800 | 2000 | 1000 | 1 | 20 | 4 | PX |  | 2.8 | 12 | 8 | 326 | 1200 | 800 | 40 | 50 | 75 | 0
0
0
ABB